May 21, 2014

Ms. Wendy Ferrill, B.E.

c/o Mississippi State Department of Health

570 East Woodrow Wilson

Jackson, MS 39215-1700

Re: Dreamland Mobile Home Park, Nicholson Water Association, PWS_ID# 0550041, Pearl Ricer County, Ref #116069

Dear Ms. Ferrill,

In reference to your April 8, 2014 letter requesting clarification for the Dreamland Mobile Home Park Upgrade/Modification project, the following information is presented for your consideration.

- We are in contact with Mississippi DEQ and have forwarded plans and specifications to them.  We are awaiting their reply.  We will forward their reply to you as soon as it is received.

- A letter from the Nicholson Water & Sewer Association is enclosed indicating the future water & sewer interconnection with that agency (item #2 and #3 on your letter).

- Water mains and sewer mains shall be separated by 10’ horizontally and 18” vertically (water above sewer) when crossing.  This information shall and has been incorporated into the design plans and specifications sheets (item #4 on your letter).

- As discussed with the Nicholson Water Association, water samples shall be collected and submitted to the Mississippi State Department of Health for analysis and approval.   Disinfection shall be using a 50 mg/l free chlorine residual for a contact time for 24 hours. This information shall and has been incorporated into the design plans and specifications sheets (items #5 and #6 on your letter).

- A title page is included (item #7 on your letter).

- Enclosed are plans & specifications for the existing mobile home park site lots delineating the lot positions (Item #8 on your letter).

Should you have any questions, or if further information if required, please feel free to contact me.  A prompt reply is greatly appreciated.

Respectfully,

Brian A. Mistich, P.E.

Mississippi Registration #20971