## 25 Year event
PROJECT: | JG Marine Shop
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR DEVELOPMENT
25 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 28742 | sqft = | 0.65983 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 24316 | sqft = | 0.55822 | Acres
c(2) = | 0.25
Green Space |  |  | 92469 | sqft = | 2.1228 | Acres
c(3) = | 0.15
Summary |  |  | 145527 | sqft = | 3.3408 | Acres
c = | 0.31484
Duration (D) = Time of concentration (TC)
where | L = | 511 | run-off length ft |  | Elev diff = | 1
| c = | 0.31484 | run-off coef
| S = | 0.19569 | percent slope
therefore | TC = D = | 16.0731 | minutes
Expected rainfall intensity | i = | 6.28 | in/hr
Q1 = | 6.6054 | cfs |  | 10% reduction | 5.9449 | cfs
POST DEVELOPMENT
25 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 31842 | sqft = | 0.73099 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 21216 | sqft = | 0.48705 | Acres
c(2) = | 0.25
Green Space |  |  | 92469 | sqft = | 2.1228 | Acres
c(3) = | 0.15
Summary |  |  | 145527 | sqft = | 3.3408 | Acres
c = | 0.32868
Duration (D) = Time of concentration (TC)
where | L = | 200 | run-off length ft |  | Elev diff = | 0.5
| c = | 0.32868 | run-off coef
| S = | 0.25 | percent slope
therefore | TC = D = | 8.3223 | minutes
Expected rainfall intensity | i = | 7.86 | in/hr
Q2 = | 8.6309 | cfs
DETENTION REQUIREMENTS
Detention required | Q2-Q1 | 2.686 | cfs
ONE HOUR DETENTION |  | 9669.6006 | cuft
DETENTION DIMENSIONS |  |  | WIDTH | 100 | feet
|  |  | LENGTH | 200 | feet
|  |  | DEPTH | 0.48348 | feet
DISCHARGE END AREA REQUIREMENTS
25 Year Frequency
[5] A=
where: A= | Discharge Area required
g= | Acceleration of gravity
c= | Discharge coefficient
h= | Hydraulic head
Q= | Flow volume from run-off
Pipe Servicing Site Drainage
Q = | 5.9449 | cfs | h = | 0.5 | feet
c = | 0.62 | coefficient | A = | 1.6908 | sqft
g = | 32.16 | ft/sec/sec
REQUIRED CONDUIT = |  |  | 17.6069 | inch inside diameter
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## Intensity calcs
ENTERED DATA = | [5 empty] | The runoff coefficient C
COMPUTED DATA= | [5 empty] | The fraction of rainfall which may be expected t become runoff
DATA FROM TABLES=
Business:
Table 1 | [5 empty] | downtown areas | 0.70 to 0.95
Rainfall Intensity (I) | [5 empty] | neighborhood areas | 0.50 to 0.70
Rainfall-Intensity-Duration-Frequency for Louisiana | [5 empty] | Residential:
Duration (t) minutes | 2 year | 10 year | 25 year | 50 year | 100 year | single-family areas | 0.30 to 0.50
5 | 6.9602 | 8.0588 | 9.0537 | 9.7926 | 10.6509 | multi units detached | 0.40 to 0.60
6 | 6.6866 | 7.8098 | 8.7827 | 9.5081 | 10.339 | multi units attached | 0.60 to 0.75
7 | 6.4347 | 7.5772 | 8.5293 | 9.2418 | 10.0475 | residential suuburban | 0.25 to 0.40
8 | 6.2021 | 7.3593 | 8.2918 | 8.9918 | 9.7744 | Apartment dwelling areas | 0.50 yo 0.70
9 | 5.9866 | 7.1549 | 8.0686 | 8.7567 | 9.5178 | Industrial:
10 | 5.7863 | 6.9626 | 7.8586 | 8.5352 | 9.2764 | light areas | 0.50 to 0.80
11 | 5.5996 | 6.7814 | 7.6605 | 8.326 | 9.0486 | heavy areas | 0.60 to 0.90
12 | 5.4252 | 6.6102 | 7.4734 | 8.1282 | 8.8335 | parks, cemeteries | 0.10 to 0.25
13 | 5.262 | 6.4484 | 7.2962 | 7.9407 | 8.6298 | playgrounds | .020 to 0.40
14 | 5.1087 | 6.295 | 7.1282 | 7.7628 | 8.4367 | unimproved areas | 0.10 to 0.30
15 | 4.9646 | 6.1495 | 6.9686 | 7.5937 | 8.2533
16 | 4.8288 | 6.0112 | 6.817 | 7.4328 | 8.0789
17 | 4.7006 | 5.8796 | 6.6725 | 7.2795 | 7.9128
18 | 4.5794 | 5.7542 | 6.5348 | 7.1331 | 7.7544
19 | 4.4647 | 5.6346 | 6.4033 | 6.9933 | 7.6032
20 | 4.3558 | 5.5203 | 6.2776 | 6.8596 | 7.4586
21 | 4.2524 | 5.4111 | 6.1573 | 6.7316 | 7.3203
22 | 4.154 | 5.3065 | 6.0422 | 6.6089 | 7.1877
23 | 4.0604 | 5.2063 | 5.9317 | 6.4911 | 7.0606
24 | 3.9711 | 5.1101 | 5.8257 | 6.3781 | 6.9386
25 | 3.8858 | 5.0178 | 5.7239 | 6.2694 | 6.8214
26 | 3.8043 | 4.9291 | 5.626 | 6.1648 | 6.7086
27 | 3.7263 | 4.8438 | 5.5318 | 6.0642 | 6.6001
28 | 3.6517 | 4.7617 | 5.4411 | 5.9672 | 6.4955
29 | 3.5801 | 4.6826 | 5.3536 | 5.8736 | 6.3948
30 | 3.5114 | 4.6064 | 5.2693 | 5.7834 | 6.2975
31 | 3.4455 | 4.5329 | 5.1879 | 5.6962 | 6.2037
32 | 3.3821 | 4.4619 | 5.1093 | 5.612 | 6.113
33 | 3.3211 | 4.3933 | 5.0333 | 5.5305 | 6.0253
34 | 3.2624 | 4.327 | 4.9598 | 5.4517 | 5.9405
35 | 3.2059 | 4.2628 | 4.8887 | 5.3754 | 5.8584
36 | 3.1514 | 4.2008 | 4.8199 | 5.3015 | 5.7789
37 | 3.0988 | 4.1407 | 4.7531 | 5.2299 | 5.7018
38 | 3.048 | 4.0824 | 4.6885 | 5.1604 | 5.6271
39 | 2.999 | 4.026 | 4.6258 | 5.093 | 5.5546
40 | 2.9516 | 3.9712 | 4.5649 | 5.0276 | 5.4842
41 | 2.9057 | 3.9181 | 4.5058 | 4.964 | 5.4159
42 | 2.8613 | 3.8665 | 4.4485 | 4.9023 | 5.3495
43 | 2.8184 | 3.8164 | 4.3927 | 4.8423 | 5.285
44 | 2.7768 | 3.7677 | 4.3385 | 4.7839 | 5.2222
45 | 2.7364 | 3.7203 | 4.2857 | 4.7271 | 5.1612
46 | 2.6973 | 3.6743 | 4.2344 | 4.6718 | 5.1017
47 | 2.6593 | 3.6295 | 4.1845 | 4.618 | 5.0439
48 | 2.6225 | 3.5859 | 4.1359 | 4.5655 | 4.9875
49 | 2.5867 | 3.5434 | 4.0885 | 4.5144 | 4.9326
50 | 2.5519 | 3.502 | 4.0423 | 4.4646 | 4.879
51 | 2.5181 | 3.4617 | 3.9973 | 4.416 | 4.8268
52 | 2.4852 | 3.4224 | 3.9534 | 4.3686 | 4.7759
53 | 2.4532 | 3.384 | 3.9106 | 4.3224 | 4.7262
54 | 2.4221 | 3.3466 | 3.8688 | 4.2772 | 4.6776
55 | 2.3918 | 3.3101 | 3.828 | 4.2331 | 4.6303
56 | 2.3623 | 3.2745 | 3.7881 | 4.1901 | 4.584
57 | 2.3336 | 3.2397 | 3.7492 | 4.148 | 4.5387
58 | 2.3055 | 3.2057 | 3.7111 | 4.1068 | 4.4945
59 | 2.2782 | 3.1725 | 3.674 | 4.0666 | 4.4513
60 | 2.2516 | 3.14 | 3.6376 | 4.0273 | 4.409