Water and sewer mains shall be separated by a minimum of 6’ when running parallel and 18” when crossing perpendicular (with the water above the sewer).

Sewer lines shall be maintained a minimum of 50’ distance from any water well.

6” collection shall be laid at a .55% slope.

6” cleanouts shall be installed on the 6” collection line every 80 linear feet.

6’ Gravity mains and 4” service laterals shall be PVC (Poly Vinyl Chloride) sewer pipe and shall comply with ASTM D3034 or UNI-B-4.  The Pipe shall be with a standard Dimension Ratio (SDR) of 35 (SDR 35).  Pipe and fittings shall have an integrated bell with elastomeric seal joints. The joints shall comply with ASTM D3212 or UNI-B-1.  Gaskets shall comply with ASTM F477.  Joint lubricants shall be as recommended by the pipe manufacturer.

PVC fittings shall manufactured by the same company that manufactured the pipe to which it is to be attached.

All Pipe fittings, cleanouts and related appurtenances shall be installed true to lines, grades and location as shown on the drawings.

All Materials shall be installed in strict conformance with the manufacturer’s recommendations.

All pipe shall be installed with the bell end facing upstream.

Interior and ends of all sewer pipes shall be thoroughly cleaned of all foreign matter before joining with the next section of the fitting.

Contractor shall pay for all sewer system testing including invert and slope verification, lamping, mandrell, pulling or any additional testing as may be required to insure system conformance.