554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

dammonengineering.com

info@dammonengineering.com

April 25, 2024

Jubilee RV Park

Hwy 434

Slidell,  La. 70461

Based on the conceptual:

1) Water production diagram of April 15, 2024  (email from David Dammon, April 17, 2024)

2) Information provided by owner, Robert Neill (free flow of +/- 120 GPM)

3) Potable water requirements for 180 RV lots (22,500 GPD)

4) An existing 10,000 gallon hydro pneumatic water storage tank

5) An intermediate 3000 gallon settlement tank

It was determined to utilize a booster pump (see attached) to bring the water pressure up t	o 50 to 60 psi.

An adequate disinfection facility was also selected. (See attached)

The existing distribution was not analyzed for fire flow.  The distribution lines appear satisfactory for potable water flow.  It was originally designed for a mobile home park.

The wastewater collection and treatment facility was not part of the analysis.

Brian Mistich

Mike serona - Mike388068@yahoo.co.us 662-288-6080