STATE OF LOUISIANA

BRIDGE CITY CENTER FOR YOUTH

SEWER SYSTEM RENOVATION

BRIDGE CITY, LOUISIANA

PROJECT NO. 08-403-11-01, PART 01 AND 08-403-04B-01, PART 20


SECTION 22 01 10.16 – VIDEO PIPING INSPECTIONS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY
A. The television camera used for the inspection shall be one specifically designed and constructed for such inspection. Lighting for the camera shall be suitable to allow a clear picture of the entire periphery of the pipe. The camera shall be operative in 100% humidity conditions. The camera, television monitor, and other components of the video system shall be capable of producing picture quality to the satisfaction of the designer; and if unsatisfactory, equipment shall be removed and no payment will be made for an unsatisfactory inspection.
B. The camera shall be moved through the line in either direction at a moderate rate, stopping when necessary to permit proper documentation of the sewer’s condition. In no case will the television camera be pulled at a speed greater than 30 feet per minute and shall stop and document each joint. Manual winches, power winches, TV cable, and powered rewinds or other devices that do not obstruct the camera view or interfere with proper documentation of the sewer conditions shall be used to move the camera through the sewer line. If, during the inspection operation, the television camera will not pass through the entire length of pipe, the Contractor shall set up his equipment so that the inspection can be performed from the opposite direction. 
C. When manually operated winches are used to pull the television camera through the line, telephones or other suitable means of communication shall be set up between the two ends of the section being inspected to insure good communications between members of the crew.
D. The importance of accurate distance measurements is emphasized. Measurement for location of defects shall be above ground by means of a meter device. Accuracy of the distance meter shall be checked by use of a walking meter, roll-a-tape, or other suitable device, and the accuracy shall be satisfactory to the independent third party inspector.
E. Documentation of the television results shall be as follows:

1. Television Inspection Logs: Electronic media location records shall be kept by the Contractor and will clearly show the location, by distance in 1/10 of a foot, from the end. In addition, other points of significance such as locations of building sewers, unusual conditions, roots, storm sewer connections, cracks, fractures, broken pipe, presence of scale and corrosion, and other discernible features, as defined in the PACP defect codes, will be recorded on electronic media and a copy of such records will be supplied through the Designer to the Owner.
2. Digital photographs of the pipe condition and all defects shall be taken by the Contractor.  Photographs shall be located by distance in 1/10 of a foot, from the end of pipe.
3. Electronic media recordings: The purpose of electronic media recording shall be to supply a visual and audio record of problem areas of the lines that may be replayed by the Owner. Each original electronic media recording of conditions and defects will be delivered to the Designer upon completion of a specific line section.

END OF SECTION 22 01 10.16
VIDEO PIPING INSPECTIONS

22 01 10.16 - 1

