Copyright 1999 AIA
MASTERSPEC - SHORT FORM
12/99

MASTERSPEC Short Form? Copyright 1999, The American Institute of Architects (AIA)

SECTION 15083 - PIPE INSULATION
PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes semirigid and flexible piping insulation, insulating cements, field-applied jackets, accessories and attachments, and sealing compounds.

1.2 SUBMITTALS

A. Product Data: Thermal conductivity, thickness, and jackets (both factory and field applied, if any), for each type of product indicated.

B. Shop Drawings:  Shop fabrication and installation details for the following:

1. Application of protective shields, saddles, and inserts at pipe hangers for each type of insulation and hanger.

2. Attachment and covering of heat trace inside insulation.

3. Insulation application at pipe expansion joints for each type of insulation.

4. Insulation application at elbows, fittings, flanges, valves, and specialties for each type of insulation.

5. Removable insulation at piping specialties and equipment connections.

6. Application of field-applied jackets.

1.3 QUALITY ASSURANCE

A. Fire-Test-Response Characteristics:  Provide products with flame-spread and smoke-developed indices of 25 and 50, respectively, according to ASTM E 84 by a testing agency acceptable to authorities having jurisdiction.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

A. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain above for nonproprietary or below for semiproprietary specification.  Refer to Division 1 Section "Product Requirements."

B. Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

1. Mineral-Fiber Insulation:

a. CertainTeed Manson.

b. Knauf FiberGlass GmbH.

c. Owens-Corning Fiberglas Corp.

d. Schuller International, Inc.

e. <Insert manufacturer.>

2. Flexible Elastomeric Thermal Insulation:

a. Armstrong World Industries, Inc.

b. Rubatex Corp.

c. <Insert manufacturer.>

3. Polyolefin Insulation:

a. Armstrong World Industries, Inc.

b. IMCOA.

c. <Insert manufacturer.>

4. Closed-Cell Phenolic-Foam Insulation:

a. Kooltherm Insulation Products, Ltd.

b. <Insert manufacturer.>

2.2 PIPE INSULATION MATERIALS

A. Mineral-Fiber Insulation:  Glass fibers bonded with a thermosetting resin complying with the following:

1. Preformed Pipe Insulation:  Comply with ASTM C 547, Type 1, with factory-applied, all-purpose, vapor-retarder jacket.

2. Blanket Insulation:  Comply with ASTM C 553, Type II, without facing.

3. Fire-Resistant Adhesive:  Comply with MIL-A-3316C Class 1, Grade A for bonding glass cloth and tape to unfaced glass-fiber insulation, for sealing edges of glass-fiber insulation, and for bonding lagging cloth to unfaced glass-fiber insulation.

4. Vapor-Retarder Mastics:  Fire- and water-resistant, vapor-retarder mastic for indoor applications.  Comply with MIL-C-19565C, Type II.

5. Mineral-Fiber Insulating Cements:  Comply with ASTM C 195.

6. Expanded or Exfoliated Vermiculite Insulating Cements:  Comply with ASTM C 196.

7. Mineral-Fiber, Hydraulic-Setting Insulating and Finishing Cement:  Comply with ASTM C 449/C 449M.

B. Flexible Elastomeric Thermal Insulation:  Closed-cell, sponge- or expanded-rubber materials.  Comply with ASTM C 534, Type I for tubular materials and Type II for sheet materials.

C. Polyolefin Insulation:  Unicellular polyethylene thermal plastic, preformed pipe insulation.  Comply with ASTM C 534, Type I, except for density.

D. Field-Applied Jackets:  ASTM C 921, Type 1, unless otherwise indicated.

1. Foil and Paper Jacket:  Laminated, glass-fiber-reinforced, flame-retardant kraft paper and aluminum foil.

2. PVC Jacket:  High-impact, ultraviolet-resistant PVC; 20 mils (0.5 mm) thick; roll stock ready for shop or field cutting and forming.

3. Standard PVC Fitting Covers:  Factory-fabricated fitting covers manufactured from 20-mil- (0.5-mm-) thick, high-impact, ultraviolet-resistant PVC.

E. Accessories and Attachments:

1. Glass Cloth and Tape:  Comply with MIL-C-20079H, Type I for cloth and Type II for tape.  Woven glass-fiber fabrics, plain weave, presized a minimum of 8 oz./sq. yd. (270 g/sq. m).

2. Bands:  3/4 inch (19 mm) wide aluminum.

3. Wire:  0.080-inch (2.0-mm), nickel-copper alloy; 0.062-inch (1.6-mm), soft-annealed, stainless steel; or 0.062-inch (1.6-mm), soft-annealed, galvanized steel.

PART 3 -  EXECUTION

3.1 GENERAL APPLICATION REQUIREMENTS

A. Surface Preparation:  Clean and dry surfaces to receive insulation.  Remove materials that will adversely affect insulation application.

B. Apply insulation materials, accessories, and finishes according to the manufacturer's written instructions; with smooth, straight, and even surfaces; and free of voids throughout the length of ducts and fittings.

C. Use accessories compatible with insulation materials and suitable for the service.  Use accessories that do not corrode, soften, or otherwise attack insulation or jacket in either wet or dry state.

D. Seal joints and seams with vapor-retarder mastic on insulation indicated to receive a vapor retarder.

E. Apply insulation with tight longitudinal seams and end joints.  Bond seams and joints with adhesive recommended by the insulation material manufacturer.

F. Apply insulation with the least number of joints practical.

G. Apply insulation over fittings and specialties, with continuous thermal and vapor-retarder integrity, unless otherwise indicated.

H. Hangers and Anchors:  Where vapor retarder is indicated, seal penetrations in insulation at hangers, supports, anchors, and other projections with vapor-retarder mastic.  Apply insulation continuously through hangers and around anchor attachments.

I. Insulation Terminations:  For insulation application where vapor retarders are indicated, seal ends with a compound recommended by the insulation material manufacturer to maintain vapor retarder.

J. Roof Penetrations:  Apply insulation for interior applications to a point even with top of roof flashing.

K. Interior Wall and Partition Penetrations:  Apply insulation continuously through walls and partitions, except fire-rated walls and partitions.

L. Floor Penetrations:  Terminate insulation at underside of floor assembly and at floor support at top of floor.

3.2 PIPE INSULATION APPLICATION SCHEDULE

A. Service:  Domestic cold water.

1. Operating Temperature:  35 to 60 deg F (2 to 15 deg C).

2. Insulation Material:  [Mineral-fiber preformed pipe] [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness:  Apply the following insulation thicknesses:

a. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert thickness.>

b. [Copper] [PVC] Pipe, <Insert Pipe Size Range>:  <Insert thickness.>

4. Vapor Retarder Required:  [Yes] [No].

B. Service:  Domestic hot and recirculated hot water.

1. Operating Temperature:  60 to 140 deg F (15 to 60 deg C).

2. Insulation Material:  [Mineral fiber] [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness: <Insert thickness.>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [None].

C. Service:  Rainwater conductors and roof drain bodies.

1. Operating Temperature:  32 to 100 deg F (0 to 38 deg C).

2. Insulation Material:  [Mineral fiber] [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness: <Insert thickness.>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [None].

5. Vapor Retarder Required:  [Yes] [No].

D. Service:  Refrigerant suction and hot-gas piping.

1. Operating Temperature:  35 to 50 deg F (2 to 10 deg C).

2. Insulation Material:  [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness: <Insert thickness.>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [None].

5. Vapor Retarder Required:  [Yes] [No].

E. Service:  Heating hot-, chilled-,  and condenser- water supply and return.

1. Operating Temperature:  100 to 200 deg F (38 to 93 deg C).

2. Insulation Material:  [Mineral fiber] [Flexible elastomeric] [Polyolefin].

3. Insulation Thickness: <Insert thickness.>

4. Field-Applied Jacket:  [Foil and paper] [PVC] [None].

5. Vapor Retarder Required:  [Yes] [No].

END OF SECTION 15083

PIPE INSULATION
15083 - 1

