section 15720

AIR HANDLING UNITS

PART 1 - GENERAL

1.01 WORK INCLUDED

A. Furnish and install air handling units and accessories as shown on the plans.

B. All systems provided shall be in compliance with code, complete and operational.  Refer to complete specifications and drawings for additional detailed requirements.  Manufacturers recommended installation guidelines shall be used if no other specific direction is given.  Bidder shall be responsible to coordinate and include in his bid all necessary appurtenances and additional material to ensure proper installation and function.  All bidders shall be responsible to review the complete set of specifications, drawings and addendums.   The completed installation shall be fully functional in accordance local codes and the intent of these specifications.
1.02 REFERENCE PUBLICATIONS

A. The following publications are incorporated by reference, and shall be the current issue at the time of bid:

1. Air Conditioning and Refrigeration Institute (ARI):

ARI 410
Forced-Circulation Air-Cooling and Air-Heating Coils

ARI 430
Central-Station Air-Handling Units

ARI Guideline D
Application and Installation of Central Station Air-Handling Units

2. Air Movement and Control Association (AMCA):

AMCA 300
Reverberant Room Method for Sound Testing of Fans

3. American Bearing Manufacturer's Association (AFBMA):

AFMBA Std 9
Load Ratings and Fatigue Life for Ball Bearings

AFMBA Std 11
Load Rating and Fatigue Life for Roller Bearings

4. American Society for Testing and Materials (ASTM):

ASTM C 1071
Thermal and Acoustical Insulation (Glass Fiber, Duct Lining Material)

ASTM F 872
Filter Units, Air Conditioning:  Viscous-Impingement Type, Cleanable

5. American Society of Heating, Refrigerating and Air Conditioning Engineers (ASHRAE):

ASHRAE 52.1
Gravimetric and Dust-Spot Procedures for Testing Air Cleaning Devices Used in General Ventilation for Removing Particulate Matter

ASHRAE 68
Laboratory Method of Testing In-Duct Sound Power Measurement Procedures for Fans

6. Institute of Environmental Sciences (IES):

IES RP-CC-001.3
HEPA and ULPA Filters

7. National Fire Protection Association (NFPA):

NFPA 70
National Electrical Code

NFPA 90A
Installation of Air Conditioning and Ventilating Systems

8. Underwriters Laboratories (UL):

UL 586
High Efficiency, Particulate, Air Filter Units

UL 900
Test Performance of Air Filter Units

PART 2 - PRODUCTS

2.01 factory-fabricated air handling units

A. Units shall be single-zone draw-through type or single-zone blow-through type as indicated.  Units shall include fans, coils, airtight insulated casing, filters, adjustable V-belt drives, belt guards for externally mounted motors, access sections where indicated, pan, and vibration-isolators, and appurtenances required for specified operation.  Each air handling unit shall have physical dimensions suitable to fit space allotted to the unit and shall have the capacity indicated.  Air handling unit shall have published ratings based on tests performed according to ARI 430.  Air unit performance shall be in accordance with scheduled requirements on drawings.
B. Casings:  Casing sections shall be 2 inch double wall type, constructed of a minimum 16 gauge galvanized steel, or 16 gauge steel outer casing protected with a corrosion resistant paint finish.  Inner casing of double-wall units shall be minimum 20 gauge  galvanized steel.  Casing shall be designed and constructed with an integral structural steel frame such that exterior panels are non-load bearing.  Exterior panels shall be individually removable.  Removal shall not affect the structural integrity of the unit.  Casings shall be provided with inspection doors, access sections, and access doors as indicated.  Inspection and access doors shall be insulated, fully gasketed, double-wall type, of minimum 16 gauge outer and 20 gauge inner panels.  Doors shall be rigid and provided with heavy duty hinges and latches.  Inspection doors shall be a minimum 12" wide by 12" high.  Access doors shall be minimum 24" wide and shall be the full height of the unit casing or a minimum of 6 ft. whichever is less.  Drain pan shall be double-bottom type constructed of 16 gauge galvanized steel, pitched to the drain connection.  Drain pans shall be constructed water tight, treated to prevent corrosion, and designed for positive condensate drainage.  When 2 or more cooling coils are used, with one stacked above the other, condensate from the upper coils shall not flow across the face of lower coils.  Intermediate drain pans or condensate collection channels and downspouts shall be provided, as required to carry condensate to the unit drain pan out of the air stream and without moisture carryover.  Each casing section handling conditioned air shall be insulated with not less than 1" thick, 1-1/2 pound density coated fibrous glass material having a thermal conductivity not greater than 0.23 Btu/hr-SF-F.  Factory applied fibrous glass insulation shall conform to ASTM C 1071, except that the minimum thickness and density requirements do not apply, and shall meet the requirements of NFPA 90A.  Foam-type insulation is not acceptable.  Foil-faced insulation shall not be an acceptable substitute for use on double-wall access doors, inspection doors, and casing sections.  Duct liner material, coating, and adhesive shall conform to fire-hazard requirements specified for duct insulation.  Exposed insulation edges and joints where insulation panels are butted together shall be protected with a metal nosing strip or shall be coated to conform to meet erosion resistance requirements of ASTM C 1071.  A latched and hinged inspection door shall be provided in the fan and coil sections.  Additional inspection doors, access doors and access sections shall be provided where indicated.

C. Heating and Cooling Coils:  Coils shall be fin-and tube type constructed of seamless copper tubes and aluminum fins mechanically bonded or soldered to the tubes.   Casing and tube support sheets shall be not lighter than 16 gauge galvanized steel, formed to provide structural strength.  When required, multiple tube supports shall be provided to prevent tube sag.  Each coil shall be tested at the factory under water at not less than 400 psi air pressure and shall be suitable for 200 psi working pressure.  Coils shall be mounted for counterflow service.  Coils shall be rated and certified according to ARI 410.

1. Water Coils:  Water coils shall be installed with a pitch of not less than 1/8" per foot of the tube length toward the drain end.  Headers shall be constructed of cast iron, welded steel or copper.  Each coil shall be provided with a plugged vent and drain connection extending through the unit casing.

D. Air Filters:  Air filters shall be listed according to requirements of UL 900.  Air filters shall be provided with filter racks.

1. Extended Surface Pleated Panel Filters: Filters shall be 2" depth, sectional, disposable type of the size indicated and shall have an average efficiency of 25 to 30% when tested according to ASHRAE 52.1.  Initial resistance at 500' per minute shall not exceed 0.36" water gauge.  Filters shall be UL Class 2.  Media shall be nonwoven cotton and synthetic fiber mat.  A wire support grid bonded to the media shall be attached to a moisture resistant fiberboard frame.  All four edges of the filter media shall be bonded to the inside of the frame to prevent air bypass and increase rigidity.

2. Replaceable Media Filters:  Replaceable media filters shall be the dry-media type, of the size required to suit the application.  Filtering media shall be not less than 2 inches thick fibrous glass media pad supported by a structural wire grid or woven wire mesh.  Pad shall be enclosed in a holding frame of not less than 16 gauge galvanized steel and equipped with quick-opening mechanism for changing filter media.  The air flow capacity of the filter shall be based on net filter face velocity not exceeding 300' per minute, with initial resistance of 0.13" water gauge.  Average efficiency shall be not less than 30% when tested according to ASHRAE 52.1.

3. Holding Frames:  Frames shall be fabricated form not lighter than 16 gauge sheet steel with rust-inhibitor coating.  Each holding frame shall be equipped with suitable filter holding devices.  Holding frame seats shall be gasketed.  All joints shall be airtight.

4. Filter Gauges:  Filter gauges shall be dial type, diaphragm actuated draft and shall be provided for all filter stations, including those filters which are furnished as integral parts of factory fabricated air handling units.  Gauges shall be at least 3-7/8" in diameter, shall have white dials with black figures, and graduations and shall have a minimum range of 1" beyond the specified final resistance for the filter bank on which each gauge is applied.  Each gauge shall incorporate a screw operated zero adjustment and shall be furnished complete with two static pressure tips with integral compression fittings, two molded plastic vent valves, two (2) 5' minimum lengths of 1/4" diameter aluminum or  vinyl tubing, and all hardware and accessories for gauge mounting.

E. Dampers:

1. Damper Assembly:  A single damper section shall have blades no longer than 48" and shall be no higher than 72".  Maximum damper blade width shall be 8".  Larger sizes shall be made from a combination of sections.  Dampers shall be steel, or other materials where shown.  Flat blades shall be made rigid by folding the edges.  All blade-operating linkages shall be within the frame so that blade-connecting devices within the same damper section will not be located directly in the air stream. Damper axles shall be 0.5" (minimum) plated steel rods supported in the damper frame by stainless steel or bronze bearings.  Blades mounted vertically shall be supported by thrust bearings.  Pressure drop through dampers shall not exceed 0.04" water gauge at 1,000 fpm in the wide-open position.  Frames shall not be less than 2" in width.  Dampers shall be tested in accordance with AMCA 500-D.
a. Operating Links:  Operating links external to dampers (such as crankarms, connecting rods, and line shafting for transmitting motion from damper actuators to dampers) shall withstand a load equal to at least twice the maximum required damper-operating force.  Rod lengths shall be adjustable.  Links shall be brass, bronze, zinc-coated steel, or stainless steel.  Working parts of joints and clevises shall be brass, bronze, or stainless steel.  Adjustments of crankarms shall control the open and closed positions of dampers.

b. Damper Types:  Dampers shall be opposed blade type.

2. Outside Air, Return Air, and Relief-Air Dampers:  The dampers shall be provided where shown.  Blades shall have interlocking edges and shall be provided with compressible seals at points of contact.  The channel frames of the dampers shall be provided with jamb seals to minimize air leakage.  Dampers shall not leak in excess of 20 cfm per square foot at 4" water gauge static pressure when closed.  Seals shall be suitable for an operating temperature range of -40( to +200( F.  Dampers shall be rated at not less than 2000 fpm air velocity.

F. Fans:  Fans shall be double-inlet, centrifugal type with each fan in a separate scroll or unhoused plenum type, as indicated on the drawings.  Fans and shafts shall be dynamically balanced prior to installation into air handling unit, and then the entire fan assembly shall be statically and dynamically balanced at the factory after it has been installed in the air handling unit.  Fans shall be mounted on steel shafts accurately ground and finished.  Fan bearings shall be sealed against dust and dirt and shall be precision self-aligning ball or roller type.  Bearing life shall be L50 rated at not less than 200,000 hours as defined by AFBMA Std 9 and AFBMA Std 11.  Bearings shall be permanently lubricated or lubricated type with lubrication fittings readily accessible at the drive side of the unit.  Bearings shall be supported by structural shapes, or die formed sheet structural members, or support plates securely attached to the unit casing.  Bearings may not be fastened directly to the unit sheet metal casing.  Fans and scrolls shall be furnished with coating indicated.  Fans shall be driven by a unit-mounted or a floor-mounted motor connected to fans by V-belt drive complete with belt guard for externally mounted motors.  Belt guards shall be the three sided enclosed type with solid or expanded metal face.  Belt drives shall be designed for not less than a 1.3 service factor based on motor nameplate rating.  Motor sheaves shall be variable pitch for 25 HP and below and fixed pitch above 25 HP as defined by ARI Guideline D.  Where fixed sheaves are required, variable pitch sheaves may be used during air balance, but shall be replaced with an appropriate fixed sheave after air balance is completed.  Variable pitch sheaves shall be selected to drive the fan at a speed that will produce the specified capacity when set at the approximate midpoint of the sheave adjustment.  Motors for V-belt drives shall be provided with adjustable bases.  Fan motors shall have totally enclosed enclosures.  Unit fan or fans shall be selected to produce the required capacity at the fan static pressure.  Sound power level shall be as indicated.  The sound power level values shall be obtained according to AMCA 300 or ASHRAE 68.

G. Access Sections and Filter/Mixing Boxes: Access sections shall be provided where indicated and shall be furnished with access doors as shown.  Access sections and filter/mixing boxes shall be constructed in a manner identical to the remainder of the unit casing and shall be equipped with access doors.  Mixing boxes shall be designed to minimize air stratification and to promote thorough mixing of the air streams.

H. Diffuser Sections:  Diffuser sections shall be furnished between the discharge of all supply fans.  Diffuser sections shall be fabricated by the unit manufacturer in a manner identical to the remainder of the unit casing, shall be designed to be airtight under positive static pressures up to 6" water gauge, and shall have an access door on each side for inspection purposes.  Diffuser section shall contain a perforated diffusion plate, fabricated of galvanized steel, Type 316 stainless steel, aluminum, or steel treated for corrosion with manufacturer's standard corrosion-resisting finish.  The diffusion plate shall be designed to accomplish uniform airflow across the down-stream coils and/or filters while reducing the higher fan outlet velocity to within plus or –5% of the required face velocity of the downstream component.

I. Factory Installed Variable Frequency Drive:

1. Acceptable Manufacturers:  Square D Company, Graham

2. Combination Variable Frequency Drive/Disconnects shall be properly sized, mounted, wired to the fan motor, and commissioned by the AHU Manufacturer.  Combination VFD disconnects shall include VFD, a circuit breaker disconnect, and a Hand-Off-Auto (HOA) switch..  An oversized control transformer, and on/off binary output, variable speed signal analog output, and all interfacing wiring shall be provided with factory mounted controls.  Factory mounting will facilitate temporary heating, cooling, ventilation, and/or timely completion of the project.

3. Disconnects:  VFD/disconnects shall be supplied with 600 VAC, 3 pole, magnetic instantaneous short circuit trip circuit breaker.  A through-the-door interlocking handle shall be spring loaded and designed to rest only in the full "ON" or "OFF" state.  A concealed defeater mechanism will allow entry into the enclosure when the handle is in the "ON" position.  A heavy-duty snap action flange operated fusible disconnect switch is also acceptable.  The blades shall be visible in the "OFF" position.  A terminal guard shall be supplied on the line side terminals.  NEMA Class R fuse clips and fuses shall be provided.

4. Enclosures:  VFD/disconnects shall have NEMA Type 1 steel open ventilated enclosures.

5. Variable Frequency Drives:  The VFD/disconnects shall be supplied with a high performance pulse width modulated (PWM) AC drive that generates a sine-code, variable voltage/frequency, three phase output for optimum speed control.  Insulated gate bipolar output transistors (IGBT's) shall ensure a low audible magnetic motor noise (@ 60 Hz) of less than 2 dB (@1 meter) above across the line operation.  Power electronics shall provide at least 96% efficiency.

6. The VFD shall have one 16 bit microprocessor control logic circuit board for all horsepower ratings.  All programming shall be maintained in nonvolatile RAM memory so the program will be maintained when power is removed.  A digital operator keypad and display shall provide local control and readout for:  run/stop/jog, speed, reset, volts, amps, kilowatts, and diagnostics.

7. Output current overload should be rated at 120% of motor FLA for one minute.  The VFD shall have the following minimal protective features:  current limited stall prevention, auto restart after momentary power loss, speed search for starting into rotating motor, anti-windmill with DC injection before start, phase to phase short circuit protection, and ground fault protection.  Ambient service temperature rating of –10( to 40( C, and humidity rating to 95% noncondensing.  The VFD shall meet or exceed UL, IEEE 444 (ANSI-C343), and IEC: 146A.

8. Factory Mounting:  VFD/disconnects shall be mounted externally on the side of the air handling unit fan section shown.  Ensure 4' of mechanical room clearance in front of the starter for serviceability per OSHA standards.

9. Factory Wiring:  VFD/disconnects shall be wired to fan motor in "liquid tight" conduit and junction boxes.  Units with factory mounted controls shall also include power wiring form the starter control transformer tot he control system transformers.  A binary start-stop signal and an analog speed signal shall be wired complete from the direct digital controller to the VFD.  Wiring methods shall comply with the National Electrical Code and NFPA 90.

10. Factory Commissioning:  Trained factory personnel shall ensure proper operation of the VFD by a thorough factory test.  The VFD shall be properly set for voltage and full load amps of the actual motor supplied.

J. Accessories  
1. Provide rated photoelectric duct smoke detectors for the unit in accordance with NFPA 90A and NEC.  The duct smoke detector can be customized to meet local codes and specifications without additional wiring.   An easy-access Test/Reset button makes it possible to test the unit with the cover on
2. Provide a matching and compatible static pressure duct controller with local display for the variable frequency drive specified herein.  The controller shall be furnished with a 0 – 3” WC range and shall control to maintain a constant static or differential pressure at a given set point.
PART 3 - EXECUTION

3.01 installation

A. Initial start-up shall be performed by the HVAC manufacturer’s representative’s office and shall ensure that the unit and controls are operating properly.  Operate units and cycle through control sequences to verify proper unit operation.  Correct any deficiencies noted.

B. All damaged surfaces of installed units shall be touched up to original factory finish.

C. Controls:  Specified controls shall be furnished by the Controls Contractor, except as previously specified or indicated.

D. All other installation procedures shall be per the manufacturer's instructions, local codes and standards.
3.02 filters

A. Provide spare set of filters for change out after starting and testing procedures are complete.
3.03 MOUNTING 

A. Concrete pad by General Contractor.  Verify size prior to pouring pad.  Provide galvanized safety pan, matching vibration isolators and condensate drain to nearest floor drain.  

END OF SECTION

15720 - 8

