March 27, 2007

Judge Jim Lamz

Slidell City Court

501 Bouscaren Drive

Slidell, LA  70458

RE:
Slidell City Court Roof Repairs

Dear Judge Lamz,

Per Our conversation on Monday the 25th of March, the following information has been gathered.

One new 5 Ton Trane packaged A/C systems cost $7,560.00, installed with crane 

Two new Trane packaged A/C systems cost $14,620.00

Delivery on the new packaged systems is three weeks from date of the order.

To repair the evaporator on the one system over the marshal’s office is $2,480.00.

Keep in mind that the life of the heat exchanger is very questionable and replacing the evaporator is just a bandage for the hot summer months ahead. 

It is my recommendation to replace the A/C system over the marshal’s office with a new system.  If the budget allows replacing a second unit at this time the worst one could be identified and be replaced.  The savings between replacing one or two systems is small at this time.

Please inform me of your decision as quickly as possible, as the new compressor for the broken unit will be installed in approximately three days.  Please be aware that once installed the compressor may only last four to six weeks before it will also self destruct because of the condition of the evaporator.

Sincerely,

Emmett G. (Pete) Dammon, PE

