COUNTRY GARDENS


Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 15815
METAL DUCTS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. Section Includes:

1. Single-wall rectangular ducts and fittings.

2. Double-wall rectangular ducts and fittings.

3. Single-wall round ducts and fittings.

4. Double-wall round ducts and fittings.

5. Sheet metal materials.

6. Duct liner.

7. Sealants and gaskets.

8. Hangers and supports.

9. Seismic-restraint devices.

1.3 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for duct construction design.

A. Delegated Duct Design:  Duct construction, including sheet metal thicknesses, seam and joint construction, reinforcements, and hangers and supports, shall comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" and performance requirements and design criteria indicated in "Duct Schedule" Article.

Retain seismic options and design criteria in first paragraph below that are approved by authorities having jurisdiction.

B. Structural Performance:  Duct hangers and supports shall withstand the effects of gravity loads and stresses within limits and under conditions described in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" 

Retain one of three subparagraphs below if retaining "SMACNA's 'Seismic Restraint Manual: Guidelines for Mechanical Systems'" option in paragraph above.  If using other seismic design criteria, delete three subparagraphs below.

Retain paragraph below to comply with LEED-NC Prerequisite EQ 1.

C. Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

1.4 SUBMITTALS

First three paragraphs below are defined in Division 1 Section "Submittal Procedures" as "Action Submittals."

A. Product Data:  For each type of the following products:

1. Liners and adhesives.

2. Sealants and gaskets.

3. Seismic-restraint devices.

B. Shop Drawings:

1. Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

2. Factory- and shop-fabricated ducts and fittings.

3. Duct layout indicating sizes, configuration, liner material, and static-pressure classes.

4. Elevation of top of ducts.

5. Dimensions of main duct runs from building grid lines.

6. Fittings.

7. Reinforcement and spacing.

8. Seam and joint construction.

9. Penetrations through fire-rated and other partitions.

10. Equipment installation based on equipment being used on Project.

11. Locations for duct accessories, including dampers, turning vanes, and access doors and panels.

12. Hangers and supports, including methods for duct and building attachment and vibration isolation.

First paragraph below is defined in Division 1 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain with "Performance Requirements" Article if design responsibilities have been delegated to Contractor.

C. Delegated-Design Submittal:

1. Sheet metal thicknesses.

2. Joint and seam construction and sealing.

3. Reinforcement details and spacing.

4. Materials, fabrication, assembly, and spacing of hangers and supports.

Retain subparagraph below if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor as another way to verify compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

Remaining paragraphs are defined in Division 1 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

D. Coordination Drawings:  Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Duct installation in congested spaces, indicating coordination with general construction, building components, and other building services.  Indicate proposed changes to duct layout.

2. Suspended ceiling components.

3. Structural members to which duct will be attached.

4. Size and location of initial access modules for acoustical tile.

5. Penetrations of smoke barriers and fire-rated construction.

6. Items penetrating finished ceiling including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

E. Welding certificates.

F. Field quality-control reports.

1.5 QUALITY ASSURANCE

Retain one of first two paragraphs below if welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Submittals" Article.  Retain first paragraph if only one AWS standard is applicable.  Retain second paragraph if more than one AWS standard is referenced.

A. Welding Qualifications:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports. AWS D9.1M/D9.1, "Sheet Metal Welding Code," for duct joint and seam welding.

B. Welding Qualifications:  Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.

2. AWS D9.1M/D9.1, "Sheet Metal Welding Code," for duct joint and seam welding.

Retain first two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.

C. ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-Up."

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

D. ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6.4.4 - "HVAC System Construction and Insulation."

Retain paragraph below for special construction.  Mockups are normally required only for static-pressure classes in excess of 3-inch wg (750 Pa) when verification of maximum allowable leakage is important.  If retaining, indicate location, size, and other details of mockups on Drawings and retain "Leakage Tests" Paragraph in "Field Quality Control" Article.

ASHRAE/IESNA 90.1 requires leakage testing for representative sections totaling no less than 25 percent of installed duct area for ducts designated to operate at a static-pressure class in excess of 3-inch wg (750 Pa).  Consider building a mockup of typical portions of the system that can be tested early in the construction process.  This standard, as enforced by some authorities having jurisdiction, requires duct systems with static-pressure classes in excess of 3-inch wg (750 Pa) to be identified on Drawings.

PART 2 -  PRODUCTS

2.1 SINGLE-WALL RECTANGULAR DUCTS AND FITTINGS

See "Static-Pressure Classes" and "Leakage and Seal Classes" articles in the Evaluations for discussion on fabrication.

A. General Fabrication Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" based on indicated static-pressure class unless otherwise indicated.

B. Transverse Joints:  Select joint types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 1-4, "Transverse (Girth) Joints," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

C. Longitudinal Seams:  Select seam types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 1-5, "Longitudinal Seams - Rectangular Ducts," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

D. Elbows, Transitions, Offsets, Branch Connections, and Other Duct Construction:  Select types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 2, "Fittings and Other Construction," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

2.2 SINGLE-WALL ROUND DUCTS AND FITTINGS

See "Static-Pressure Classes" and "Leakage and Seal Classes" articles in the Evaluations for discussion on fabrication.

A. General Fabrication Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 3, "Round, Oval, and Flexible Duct," based on indicated static-pressure class unless otherwise indicated.

Retain subparagraph below to require factory-fabricated, single-wall round and flat-oval ducts and fittings; delete to allow shop-fabricated ducts and fittings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain subparagraph and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

a. Lindab Inc.

b. McGill AirFlow LLC.

c. SEMCO Incorporated.

d. Sheet Metal Connectors, Inc.

e. Spiral Manufacturing Co., Inc.

B. Flat-Oval Ducts:  Indicated dimensions are the duct width (major dimension) and diameter of the round sides connecting the flat portions of the duct (minor dimension).

C. Transverse Joints:  Select joint types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-2, "Transverse Joints - Round Duct," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

Option in subparagraph below is SMACNA?s requirement.  Insert smaller dimension for more stringent requirement.

1. Transverse Joints in Ducts Larger Than 60 Inches in Diameter:  Flanged.

D. Longitudinal Seams:  Select seam types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-1, "Seams - Round Duct and Fittings," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

1. Fabricate round ducts larger than 90 inches in diameter with butt-welded longitudinal seams.

2. Fabricate flat-oval ducts larger than 72 inches in width (major dimension) with butt-welded longitudinal seams.

E. Tees and Laterals:  Select types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-4, "90 Degree Tees and Laterals," and Figure 3-5, "Conical Tees," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

2.3 SHEET METAL MATERIALS

A. General Material Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

See "Sheet Metal Materials" Article in the Evaluations for discussion on applicable materials and coatings in first six paragraphs below.

B. Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

1. Galvanized Coating Designation:  G60.

2. Finishes for Surfaces Exposed to View:  Mill phosphatized.

C. Aluminum Sheets:  Comply with ASTM B 209 Alloy 3003, H14 temper; with mill finish for concealed ducts, and standard, one-side bright finish for duct surfaces exposed to view.

Antimicrobial coating in first paragraph below is an optional feature and usually applied only after fabrication to ducts fabricated with galvanized sheet steel.  See Evaluations for discussion on coatings.

D. Factory- or Shop-Applied Antimicrobial Coating:

1. Apply to the surface of sheet metal that will form the interior surface of the duct.  An untreated clear coating shall be applied to the exterior surface.

2. Antimicrobial compound shall be tested for efficacy by an NRTL and registered by the EPA for use in HVAC systems.

3. Coating containing the antimicrobial compound shall have a hardness of 2H, minimum, when tested according to ASTM D 3363.

4. Surface-Burning Characteristics:  Maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

5. Shop-Applied Coating Color:  Black.

6. Antimicrobial coating on sheet metal is not required for duct containing liner treated with antimicrobial coating.

E. Reinforcement Shapes and Plates:  ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

1. Where black- and galvanized-steel shapes and plates are used to reinforce aluminum ducts, isolate the different metals with butyl rubber, neoprene, or EPDM gasket materials.

F. Tie Rods:  Galvanized steel, 1/4-inch minimum diameter for lengths 36 inches or less; 3/8-inch minimum diameter for lengths longer than 36 inches.

2.4 SEALANT AND GASKETS

A. General Sealant and Gasket Requirements:  Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

See SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for discussion on seam and joint sealing methods and their applications.  Retain one or more of first three paragraphs below, and identify which sealing system applies to which duct system in the "Duct Schedule" Article.

Retain one of first two paragraphs below.  If retaining second paragraph, verify acceptability with authorities having jurisdiction.

B. Water-Based Joint and Seam Sealant:

1. Application Method:  Brush on.

2. Solids Content:  Minimum 65 percent.

3. Shore A Hardness:  Minimum 20.

4. Water resistant.

5. Mold and mildew resistant.

6. VOC:  Maximum 75 g/L (less water).

7. Maximum Static-Pressure Class:  10-inch wg, positive and negative.

8. Service:  Indoor or outdoor.

9. Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

C. Solvent-Based Joint and Seam Sealant:

1. Application Method:  Brush on.

2. Base:  Synthetic rubber resin.

3. Solvent:  Toluene and heptane.

4. Solids Content:  Minimum 60 percent.

5. Shore A Hardness:  Minimum 60.

6. Water resistant.

7. Mold and mildew resistant.

Retain one of first two subparagraphs below.  Retain first subparagraph if low-emitting materials are required for LEED-NC Credit EQ 4.1.

8. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

9. VOC:  Maximum 395 g/L.

10. Maximum Static-Pressure Class:  10-inch wg, positive or negative.

11. Service:  Indoor or outdoor.

12. Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

D. Flanged Joint Sealant:  Comply with ASTM C 920.

1. General:  Single-component, acid-curing, silicone, elastomeric.

2. Type:  S.

3. Grade:  NS.

4. Class:  25.

5. Use:  O.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

6. For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

E. Flange Gaskets:  Butyl rubber, neoprene, or EPDM polymer with polyisobutylene plasticizer.

O-ring seals are generally available for duct fittings 3 to 24 inches (76 to 610 mm) in diameter.

F. Round Duct Joint O-Ring Seals:

1. Seal shall provide maximum leakage class of 3 cfm/100 sq. ft. at 1-inch wg and shall be rated for 10-inch wg static-pressure class, positive or negative.

Retain one or both subparagraphs below.  These are proprietary seals provided on factory-fabricated, round duct fitting joints and constructed with specific dimensions to ensure a proper seal.

2. EPDM O-ring to seal in concave bead in coupling or fitting spigot.

3. Double-lipped, EPDM O-ring seal, mechanically fastened to factory-fabricated couplings and fitting spigots.

2.5 HANGERS AND SUPPORTS

Indicate the extent of corrosive environment on Drawings.

A. Hanger Rods for Noncorrosive Environments:  Cadmium-plated steel rods and nuts.

B. Hanger Rods for Corrosive Environments:  Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

C. Strap and Rod Sizes:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 4-1, "Rectangular Duct Hangers Minimum Size," and Table 4-2, "Minimum Hanger Sizes for Round Duct."

D. Steel Cables for Galvanized-Steel Ducts:  Galvanized steel complying with ASTM A 603.

E. Steel Cables for Stainless-Steel Ducts:  Stainless steel complying with ASTM A 492.

F. Steel Cable End Connections:  Cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

G. Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

H. Trapeze and Riser Supports:

1. Supports for Galvanized-Steel Ducts:  Galvanized-steel shapes and plates.

2. Supports for Stainless-Steel Ducts:  Stainless-steel shapes and plates.

3. Supports for Aluminum Ducts:  Aluminum or galvanized steel coated with zinc chromate.

PART 3 -  EXECUTION

3.1 DUCT INSTALLATION

Coordinate duct layout and duct accessory arrangement with Drawings.

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of duct system.  Indicated duct locations, configurations, and arrangements were used to size ducts and calculate friction loss for air-handling equipment sizing and for other design considerations.  Install duct systems as indicated unless deviations to layout are approved on Shop Drawings and Coordination Drawings.

B. Install ducts according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" unless otherwise indicated.

C. Install round ducts in maximum practical lengths.

D. Install ducts with fewest possible joints.

E. Install factory- or shop-fabricated fittings for changes in direction, size, and shape and for branch connections.

F. Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

G. Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

H. Install ducts with a clearance of 1 inch, plus allowance for insulation thickness.

I. Route ducts to avoid passing through transformer vaults and electrical equipment rooms and enclosures.

J. Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges of same metal thickness as the duct.  Overlap openings on four sides by at least 1-1/2 inches.

K. Where ducts pass through fire-rated interior partitions and exterior walls, install fire dampers.  Comply with requirements in Division 15 Section "Duct Accessories" for fire and smoke dampers.

L. Protect duct interiors from moisture, construction debris and dust, and other foreign materials. Comply with SMACNA's "Duct Cleanliness for New Construction Guidelines."

3.2 DUCT SEALING

Retain one of two paragraphs below.  Retain first paragraph if retaining subparagraphs for seal class and leakage class in "Duct Schedule" Article; otherwise, delete first and retain second paragraph.

A. Seal ducts for duct static-pressure, seal classes, and leakage classes specified in "Duct Schedule" Article according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.1 - "Duct Sealing" requires a minimum seal class for various duct locations and pressures indicated in paragraph below.

B. Seal ducts to the following seal classes according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible":

1. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

2. Outdoor, Supply-Air Ducts:  Seal Class A.

3. Outdoor, Exhaust Ducts:  Seal Class C.

4. Outdoor, Return-Air Ducts:  Seal Class C.

5. Unconditioned Space, Supply-Air Ducts in Pressure Classes 2-Inch wg and Lower:  Seal Class B.

6. Unconditioned Space, Supply-Air Ducts in Pressure Classes Higher Than2-Inch wg:  Seal Class A.

7. Unconditioned Space, Exhaust Ducts:  Seal Class C.

8. Unconditioned Space, Return-Air Ducts:  Seal Class B.

9. Conditioned Space, Supply-Air Ducts in Pressure Classes2-Inch wg. and Lower:  Seal Class C.

10. Conditioned Space, Supply-Air Ducts in Pressure Classes Higher Than 2-Inch wg :  Seal Class B.

11. Conditioned Space, Exhaust Ducts:  Seal Class B.

12. Conditioned Space, Return-Air Ducts:  Seal Class C.

3.3 HANGER AND SUPPORT INSTALLATION

A. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 4, "Hangers and Supports."

Verify attachment selection and spacing in first two paragraphs below with structural engineer.

B. Building Attachments:  Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Where practical, install concrete inserts before placing concrete.

2. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

3. Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 4 inches thick.

4. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches thick.

Retain subparagraph below for Projects that require seismic restraints.

5. Do not use powder-actuated concrete fasteners for seismic restraints.

C. Hanger Spacing:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 4-1, "Rectangular Duct Hangers Minimum Size," and Table 4-2, "Minimum Hanger Sizes for Round Duct," for maximum hanger spacing; install hangers and supports within 24 inches of each elbow and within 48 inches of each branch intersection.

D. Hangers Exposed to View:  Threaded rod and angle or channel supports.

E. Support vertical ducts with steel angles or channel secured to the sides of the duct with welds, bolts, sheet metal screws, or blind rivets; support at each floor and at a maximum intervals of 16 feet.

F. Install upper attachments to structures.  Select and size upper attachments with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain first paragraph below for ducts in pressure classes 3-inch wg (750 Pa) and higher or if applying for LEED credits.  It may not be economically practical to test ducts in pressure classes less than 3-inch wg (750 Pa).

B. Leakage Tests:

1. Comply with SMACNA's "HVAC Air Duct Leakage Test Manual."  Submit a test report for each test.

2. Test the following systems:

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.2 - "Duct Leakage Tests" requires leak testing of at least 25 percent of total installed duct area with a pressure class in excess of 3-inch wg (750 Pa).  Retain first subparagraph below for minimum requirements if applying for LEED certification or complying with ASHRAE/IESNA 90.1-2004.  To define more stringent requirements, retain subsequent subparagraphs as applicable and delete first subparagraph.  Consider cost impact when specifying the extent of duct area to be tested.  It is not common to leak test all ducts or ducts with a pressure class less than 3-inch wg (750 Pa).

a. Ducts with a Pressure Class Higher Than 3-Inch wg:  Test representative duct sections, totaling no less than 25 percent of total installed duct area for each designated pressure class.

b. Supply Ducts with a Pressure Class of 1-Inch wg or Higher:  Test representative duct sections totaling no less than 50 percent of total installed duct area for each designated pressure class.

c. Return Ducts with a Pressure Class of 1-Inch wg or Higher:  Test representative duct sections, selected by Architect from sections installed, totaling no less than 50 percent of total installed duct area for each designated pressure class.

d. Exhaust Ducts with a Pressure Class of 1-Inch wg or Higher:  Test representative duct sections totaling no less than 50 percent of total installed duct area for each designated pressure class.

e. Outdoor Air Ducts with a Pressure Class of 1-Inch wg or Higher:  Test representative duct sections totaling no less than 50 percent of total installed duct area for each designated pressure class.

3. Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

4. Test for leaks before applying external insulation.

5. Conduct tests at static pressures equal to maximum design pressure of system or section being tested.  If static-pressure classes are not indicated, test system at maximum system design pressure.  Do not pressurize systems above maximum design operating pressure.

6. Give seven days' advance notice for testing.

Retain first paragraph below if duct cleaning is required.  Text was taken from NADCA ACR, dated 2005.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

C. Duct System Cleanliness Tests:

1. Visually inspect duct system to ensure that no visible contaminants are present.

2. Test sections of metal duct system, chosen randomly by Owner, for cleanliness according to "Vacuum Test" in NADCA ACR, "Assessment, Cleaning and Restoration of HVAC Systems."

a. Acceptable Cleanliness Level:  Net weight of debris collected on the filter media shall not exceed 0.75 mg/100 sq. cm.

See Division 1 Section "Quality Requirements" for retesting and reinspecting requirements and Division 1 Section "Execution Requirements" for requirements for correcting the Work.

D. Duct system will be considered defective if it does not pass tests and inspections.

E. Prepare test and inspection reports.

3.5 DUCT SCHEDULE

A. Fabricate ducts with galvanized sheet steel.
Retain applicable subparagraphs in this article to set criteria for pressure class, duct seal-class level, and duct-leakage class; or delete applicable subparagraphs and indicate pressure class, duct seal-class level, and duct-leakage class on Drawings.  If retaining duct seal and leakage requirements in this article, retain first paragraph in "Duct Sealing" Article.  Both seal class and leakage class are included in this article and either one can be deleted, or both can remain if they are consistent.

Paragraphs below are examples of broad system classifications.  Revise to suit Project or indicate requirements on Drawings if a more refined classification is required.

See ASHRAE duct leakage recommendations in 2005 ASHRAE HANDBOOK - "Fundamentals," Chapter 35, "Duct Design," Table 7, "Recommended Ductwork Leakage Class by Duct Type."

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.1 - "Duct Sealing" requires a minimum seal-class level (A, B, or C) for various duct locations and pressures and specifies seal-class levels for joints and seams in ducts located outdoors, in unconditioned spaces, and in conditioned spaces.  Retain second paragraph in "Duct Sealing" Article if applying for LEED certification and requirements are not defined in this article or on Drawings.

B. Exhaust Ducts:

1. Ducts Connected to Fans Exhausting (ASHRAE 62.1, Class 1 and 2) Air:

a. Pressure Class:  Negative 1-inch wg.

b. Minimum SMACNA Seal Class:  A if negative pressure, and A if positive pressure.

c. SMACNA Leakage Class for Rectangular:  12.

d. SMACNA Leakage Class for Round and Flat Oval:  6.

2. Ducts Connected to Air-Handling Units:

a. Pressure Class:  Positive or negative 2-inch wg.

b. Minimum SMACNA Seal Class:  A if negative pressure, and A if positive pressure.

c. SMACNA Leakage Class for Rectangular:  6.

d. SMACNA Leakage Class for Round and Flat Oval:  3.

Retain first subparagraph below unless fire-rated, factory-fabricated grease ducts for Type I commercial kitchen hoods are specified in Division 15 Section "Breechings, Chimneys, and Stacks." Factory-fabricated and -insulated grease ducts can be installed with reduced clearance to combustible construction.

3. Ducts Connected to Equipment Not Listed Above:

a. Pressure Class:  Positive or negative 2-inch wg.

b. Minimum SMACNA Seal Class:  A if negative pressure, and A if positive pressure.

c. SMACNA Leakage Class for Rectangular:  6>.

d. SMACNA Leakage Class for Round and Flat Oval:  3.

LEED-NC Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."  If using interstitial insulation alone to satisfy thermal requirements, verify that material selected is available in thickness needed to provide thermal performance without jeopardizing other requirements.

C. Elbow Configuration:

Retain one of first two subparagraphs below.  Retain first subparagraph to set different requirements for various velocities.  Retain second subparagraph to set the same requirements for all velocities.

1. Rectangular Duct:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-2, "Rectangular Elbows."

a. Velocity 1000 fpm or Lower:

1) Radius Type RE 1 with minimum 0.5 radius-to-diameter ratio.

2) Mitered Type RE 4 without vanes.

b. Velocity 1000 to 1500 fpm:

1) Radius Type RE 1 with minimum 1.0 radius-to-diameter ratio.

2) Radius Type RE 3 with minimum 0.5 radius-to-diameter ratio and two vanes.

3) Mitered Type RE 2 with vanes complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-3, "Vanes and Vane Runners," and Figure 2-4, "Vane Support in Elbows."

c. Velocity 1500 fpm or Higher:

1) Radius Type RE 1 with minimum 1.5 radius-to-diameter ratio.

2) Radius Type RE 3 with minimum 1.0 radius-to-diameter ratio and two vanes.

3) Mitered Type RE 2 with vanes complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-3, "Vanes and Vane Runners," and Figure 2-4, "Vane Support in Elbows."

2. Rectangular Duct:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-2, "Rectangular Elbows."

a. Radius Type RE 1 with minimum 1.5 radius-to-diameter ratio.

b. Radius Type RE 3 with minimum 1.0 radius-to-diameter ratio and two vanes.

c. Mitered Type RE 2 with vanes complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-3, "Vanes and Vane Runners," and Figure 2-4, "Vane Support in Elbows."

3. Round Duct:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-3, "Round Duct Elbows."

a. Minimum Radius-to-Diameter Ratio and Elbow Segments:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 3-1, "Mitered Elbows."  Elbows with less than 90-degree change of direction have proportionately fewer segments.

Retain first three subparagraphs below, or delete and retain fourth subparagraph.

1) Velocity 1000 fpm or Lower:  0.5 radius-to-diameter ratio and three segments for 90-degree elbow.

2) Velocity 1000 to 1500 fpm:  1.0 radius-to-diameter ratio and four segments for 90-degree elbow.

3) Velocity 1500 fpm or Higher:  1.5 radius-to-diameter ratio and five segments for 90-degree elbow.

4) Radius-to Diameter Ratio:  1.5.

b. Round Elbows, 12 Inches and Smaller in Diameter:  Stamped or pleated.

c. Round Elbows, 14 Inches and Larger in Diameter:  Standing seam.

Delete paragraph below if branch fittings are detailed on Drawings.

D. Branch Configuration:

1. Rectangular Duct:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-6, "Branch Connections."

a. Rectangular Main to Rectangular Branch:  45-degree entry.

b. Rectangular Main to Round Branch:  Spin in.

2. Round and Flat Oval:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-4, "90 Degree Tees and Laterals," and Figure 3-5, "Conical Tees."  Saddle taps are permitted in existing duct.

a. Velocity 1000 fpm or Lower:  90-degree tap.

b. Velocity 1000 to 1500 fpm:  Conical tap.

c. Velocity 1500 fpm or Higher:  45-degree lateral.

END OF DOCUMENT
METAL DUCTS
15815 - 12

