COUNTRY GARDENS


SECTION 16140
WIRING DEVICES
SECTION 16140 - WIRING DEVICES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

1. Receptacles, receptacles with integral GFCI, and associated device plates.

2. Twist-locking receptacles.

3. Receptacles with integral surge suppression units.

4. Wall-box motion sensors.

5. Isolated-ground receptacles.

6. Hospital-grade receptacles.

7. Snap switches and wall-box dimmers.

8. Solid-state fan speed controls.

9. Wall-switch and exterior occupancy sensors.

10. Communications outlets.

11. Pendant cord-connector devices.

12. Cord and plug sets.

13. Floor service outlets, poke-through assemblies, service poles, and multioutlet assemblies.

1.3 DEFINITIONS

Retain term and abbreviations that remain after this Section has been edited.

A. EMI:  Electromagnetic interference.

B. GFCI:  Ground-fault circuit interrupter.

C. Pigtail:  Short lead used to connect a device to a branch-circuit conductor.

D. RFI:  Radio-frequency interference.

E. TVSS:  Transient voltage surge suppressor.

F. UTP:  Unshielded twisted pair.

1.4 SUBMITTALS

A. Product Data:  For each type of product indicated.

B. Shop Drawings:  List of legends and description of materials and process used for premarking wall plates.

Retain first paragraph below if products have critical features needing hands-on appraisal.

C. Samples:  One for each type of device and wall plate specified, in each color specified.  Devices/Receptacles to be Brown.
D. Field quality-control test reports.

E. Operation and Maintenance Data:  For wiring devices to include in all manufacturers' packing label warnings and instruction manuals that include labeling conditions.

1.5 QUALITY ASSURANCE

A. Source Limitations:  Obtain each type of wiring device and associated wall plate through one source from a single manufacturer.  Insofar as they are available, obtain all wiring devices and associated wall plates from a single manufacturer and one source.

B. Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

C. Comply with NFPA 70.

1.6 COORDINATION

Retain this Article if receptacles for Owner-furnished equipment with plugs have unknown or special configurations.

A. Receptacles for Owner-Furnished Equipment:  Match plug configurations.

Retain subparagraph below if cord and plug sets are specified in Part 2.

1. Cord and Plug Sets:  Match equipment requirements.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

A. Manufacturers' Names:  Shortened versions (shown in parentheses) of the following manufacturers' names are used in other Part 2 articles:

Manufacturers listed below produce an extensive line of nationally distributed wiring devices.  Add manufacturers if desired.

1. Cooper Wiring Devices; a division of Cooper Industries, Inc. (Cooper).

2. Hubbell Incorporated; Wiring Device-Kellems (Hubbell).

3. Leviton Mfg. Company Inc. (Leviton).

4. Pass & Seymour/Legrand; Wiring Devices & Accessories (Pass & Seymour).

2.2 STRAIGHT BLADE RECEPTACLES

A. Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

Catalog numbers in subparagraphs below are for 20-A devices; revise catalog numbers if 15-A devices are desired.

a. Cooper; 5351 (single), 5352 (duplex).

b. Hubbell; HBL5351 (single), CR5352 (duplex).

c. Leviton; 5891 (single), 5352 (duplex).

d. Pass & Seymour; 5381 (single), 5352 (duplex).

Isolated-ground receptacles are available in a variety of configurations and ratings including locking-blade types up to 50 A and 250 V.  Revise first paragraph and subparagraphs below to suit Project; indicate different types on Drawings.

B. Isolated-Ground, Duplex Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Hubbell; CR 5253IG.

b. Leviton; 5362-IG.

c. Pass & Seymour; IG6300.

2. Description:  Straight blade; equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

C. Tamper-Resistant Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; TR8300.

b. Hubbell; HBL8300SG.

c. Leviton; 8300-SGG.

d. Pass & Seymour; 63H.

2. Description:  Labeled to comply with NFPA 70, "Health Care Facilities" Article, "Pediatric Locations" Section.

2.3 GFCI RECEPTACLES

Non-feed-through-type GFCI unit may be selected where no protection of downstream receptacles is required.

A. General Description:  Straight blade, feed-through type.  Comply with NEMA WD 1, NEMA WD 6, UL 498, and UL 943, Class A, and include indicator light that is lighted when device is tripped.

B. Duplex GFCI Convenience Receptacles, 125 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

Catalog numbers in subparagraphs below are for feed-through types, arranged to protect receptacles downstream on the same circuit; revise catalog numbers if non-feed-through types are required.

a. Cooper; GF20.

b. Pass & Seymour; 2084.

2.4 TVSS RECEPTACLES

See Editing Instruction No. 3 in the Evaluations for information on TVSS ratings.

A. General Description:  Comply with NEMA WD 1, NEMA WD 6, UL 498, and UL 1449, with integral TVSS in line to ground, line to neutral, and neutral to ground.

1. TVSS Components:  Multiple metal-oxide varistors; with a nominal clamp-level rating of 400 volts and minimum single transient pulse energy dissipation of 240 J, according to IEEE C62.41.2 and IEEE C62.45.

2. Active TVSS Indication:  Visual and audible, with light visible in face of device to indicate device is "active" or "no longer in service."

B. Duplex TVSS Convenience Receptacles:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

Catalog numbers in first three subparagraphs below are for products with visual-only indication.

a. Cooper; 5362BLS.

b. Hubbell; HBL5362SA.

c. Leviton; 5380.

2. Description:  Straight blade, 125 V, 20 A; NEMA WD 6 configuration 5-20R.

C. Isolated-Ground, Duplex Convenience Receptacles:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; IG5362BLS.

b. Hubbell; IG5362SA.

c. Leviton; 5380-IG.

2. Description:  Straight blade, 125 V, 20 A; NEMA WD 6 configuration 5-20R.  Equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

2.5 TWIST-LOCKING RECEPTACLES

A. Single Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration L5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; L520R.

b. Hubbell; HBL2310.

c. Leviton; 2310.

d. Pass & Seymour; L520-R.

B. Isolated-Ground, Single Convenience Receptacles, 125 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Hubbell; IG2310.

b. Leviton; 2310-IG.

2. Description:  Comply with NEMA WD 1, NEMA WD 6 configuration L5-20R, and UL 498.  Equipment grounding contacts shall be connected only to the green grounding screw terminal of the device and with inherent electrical isolation from mounting strap.  Isolation shall be integral to receptacle construction and not dependent on removable parts.

2.6 PENDANT CORD-CONNECTOR DEVICES

Revise NEMA configuration in paragraph below to suit Project.  Delete "External Cable Grip" Subparagraph if not required.

A. Description:  Matching, locking-type plug and receptacle body connector; NEMA WD 6 configurations L5-20P and L5-20R, heavy-duty grade.

1. Body:  Nylon with screw-open cable-gripping jaws and provision for attaching external cable grip.

2. External Cable Grip:  Woven wire-mesh type made of high-strength galvanized-steel wire strand, matched to cable diameter, and with attachment provision designed for corresponding connector.

2.7 CORD AND PLUG SETS

Retain this Article if cord and plug sets for equipment are furnished by Owner or are specified in other Sections.  Coordinate with other Sections and with Part 3.

A. Description:  Match voltage and current ratings and number of conductors to requirements of equipment being connected.

1. Cord:  Rubber-insulated, stranded-copper conductors, with Type SOW-A jacket; with green-insulated grounding conductor and equipment-rating ampacity plus a minimum of 30 percent.

2. Plug:  Nylon body and integral cable-clamping jaws.  Match cord and receptacle type for connection.

2.8 SNAP SWITCHES

A. Comply with NEMA WD 1 and UL 20.

B. Switches, 120/277 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

Catalog numbers in subparagraphs below are for 20-A devices; revise catalog numbers if 15-A devices are desired.

a. Cooper; 2221 (single pole), 2222 (two pole), 2223 (three way), 2224 (four way).

b. Hubbell; CS1221 (single pole), CS1222 (two pole), CS1223 (three way), CS1224 (four way).

c. Leviton; 1221-2 (single pole), 1222-2 (two pole), 1223-2 (three way), 1224-2 (four way).

d. Pass & Seymour; 20AC1 (single pole), 20AC2 (two pole), 20AC3 (three way), 20AC4 (four way).

C. Pilot Light Switches, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; 2221PL for 120 V and 277 V.

b. Hubbell; HPL1221PL for 120 V and 277 V.

c. Leviton; 1221-PLR for 120 V, 1221-7PLR for 277 V.

d. Pass & Seymour; PS20AC1-PLR for 120 V.

2. Description:  Single pole, with neon-lighted handle, illuminated when switch is "ON."

D. Key-Operated Switches, 120/277 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; 2221L.

b. Hubbell; HBL1221L.

c. Leviton; 1221-2L.

d. Pass & Seymour; PS20AC1-L.

2. Description:  Single pole, with factory-supplied key in lieu of switch handle.

E. Single-Pole, Double-Throw, Momentary Contact, Center-Off Switches, 120/277 V, 20 A; for use with mechanically held lighting contactors.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; 1995.

b. Hubbell; HBL1557.

c. Leviton; 1257.

d. Pass & Seymour; 1251.

F. Key-Operated, Single-Pole, Double-Throw, Momentary Contact, Center-Off Switches, 120/277 V, 20 A; for use with mechanically held lighting contactors, with factory-supplied key in lieu of switch handle.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

a. Cooper; 1995L.

b. Hubbell; HBL1557L.

c. Leviton; 1257L.

d. Pass & Seymour; 1251L.

2.9 WALL PLATES

A. Single and combination types to match corresponding wiring devices.

B. Wet-Location, Weatherproof Cover Plates:  NEMA 250, complying with type 3R weather-resistant  with lockable cover.

PART 3 -  EXECUTION

3.1 INSTALLATION

NECA 1 referenced in paragraph below includes device mounting-height requirements.  See "Product Selection and Application Considerations" Article in the Evaluations for device mounting heights in that standard.

A. Comply with NECA 1, including the mounting heights listed in that standard, unless otherwise noted.

See Editing Instruction No. 4 in the Evaluations for timing and sequencing of construction to assist in avoiding contamination of devices during construction.

B. Coordination with Other Trades:

1. Take steps to insure that devices and their boxes are protected.  Do not place wall finish materials over device boxes and do not cut holes for boxes with routers that are guided by riding against outside of the boxes.

2. Keep outlet boxes free of plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other material that may contaminate the raceway system, conductors, and cables.

3. Install device boxes in brick or block walls so that the cover plate does not cross a joint unless the joint is troweled flush with the face of the wall.

4. Install wiring devices after all wall preparation, including painting, is complete.

C. Conductors:

1. Do not strip insulation from conductors until just before they are spliced or terminated on devices.

2. Strip insulation evenly around the conductor using tools designed for the purpose.  Avoid scoring or nicking of solid wire or cutting strands from stranded wire.

3. The length of free conductors at outlets for devices shall meet provisions of NFPA 70, Article 300, without pigtails.

4. Existing Conductors:

a. Cut back and pigtail, or replace all damaged conductors.

b. Straighten conductors that remain and remove corrosion and foreign matter.

c. Pigtailing existing conductors is permitted provided the outlet box is large enough.

D. Device Installation:

1. Replace all devices that have been in temporary use during construction or that show signs that they were installed before building finishing operations were complete.

2. Keep each wiring device in its package or otherwise protected until it is time to connect conductors.

3. Do not remove surface protection, such as plastic film and smudge covers, until the last possible moment.

4. Connect devices to branch circuits using pigtails that are not less than 6 inches in length.

5. When there is a choice, use side wiring with binding-head screw terminals.  Wrap solid conductor tightly clockwise, 2/3 to 3/4 of the way around terminal screw.

6. Use a torque screwdriver when a torque is recommended or required by the manufacturer.

7. When conductors larger than No. 12 AWG are installed on 15- or 20-A circuits, splice No. 12 AWG pigtails for device connections.

8. Tighten unused terminal screws on the device.

9. When mounting into metal boxes, remove the fiber or plastic washers used to hold device mounting screws in yokes, allowing metal-to-metal contact.

E. Receptacle Orientation:

Retain subparagraph below if the position of the ground pin is important for consistency.  Trade and professional literature is inconsistent in recommending benefits of either orientation.

1. Install ground pin of vertically mounted receptacles down, and on horizontally mounted receptacles to the left.

Recommendation in subparagraph below is made in IEEE 602.

2. Install hospital-grade receptacles in patient-care areas with the ground pin or neutral blade at the top.

F. Device Plates:  Do not use oversized or extra-deep plates.  Repair wall finishes and remount outlet boxes when standard device plates do not fit flush or do not cover rough wall opening.

G. Dimmers:

1. Install dimmers within terms of their listing.

2. Install unshared neutral conductors on line and load side of dimmers according to manufacturers' device listing conditions in the written instructions.

Coordinate two paragraphs below with Drawings.

H. Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical and with grounding terminal of receptacles on top.  Group adjacent switches under single, multigang wall plates.

3.2 IDENTIFICATION

A. Comply with Division 16 Section "Electrical Identification."

1. Receptacles:  Identify panelboard and circuit number from which served.  Use stamped black-filled lettering on face of plate, and durable wire markers or tags inside outlet boxes.

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

1. In healthcare facilities, prepare reports that comply with recommendations in NFPA 99.

2. Test Instruments:  Use instruments that comply with UL 1436.

3. Test Instrument for Convenience Receptacles:  Digital wiring analyzer with digital readout or illuminated LED indicators of measurement.

B. Tests for Convenience Receptacles:

1. Line Voltage:  Acceptable range is 105 to 132 V.

2. Percent Voltage Drop under 15-A Load:  A value of 6 percent or higher is not acceptable.

3. Ground Impedance:  Values of up to 2 ohms are acceptable.

4. GFCI Trip:  Test for tripping values specified in UL 1436 and UL 943.

5. Using the test plug, verify that the device and its outlet box are securely mounted.

6. The tests shall be diagnostic, indicating damaged conductors, high resistance at the circuit breaker, poor connections, inadequate fault current path, defective devices, or similar problems.  Correct circuit conditions, remove malfunctioning units and replace with new ones, and retest as specified above.

C. Test straight blade hospital-grade convenience outlets for the retention force of the grounding blade according to NFPA 99.  Retention force shall be not less than 4 oz.

END OF DOCUMENT
WIRING DEVICES

16140 - 7

