7/1/2008 2:59 PM

TOWERS BUILDING

ELECTRICAL DRAWINGS

CLARIFICATIONS AND CORRECTIONS

1st Floor E-1PRestroom GFI Receptacles were wired together, as well as with other Receptacles in Room 111.  Two Circuits were added- Nos.15, for Room 111 Receptacles and 16, for Men’s Restroom GFI receptacles.

The two Receptacles tied to Ladies Restroom GFI Receptacles were added to Circuit PP1-5.
E-9
Panel PP-1, Circuit 3- Location Description clarification only.
2nd Floor E-2PLadies Restroom GFI Receptacle was moved from near the Window Wall to near the Lavatory Counter Top, as prescribed by the NEC.  One Circuit was added- Panel PP2, Circuit 29.

One Receptacle was deleted from Panel PP-2, Circuit 11, Mezzanine Receptacles.  There were too many on this circuit.

VAV Heater 1-4 was missing at AHU 1, Mezzanine and was added.
E-9
Panel PP-2, Circuit 5- Location Description clarification only.

The Volt Amps for Panel PP-2, Circuit 11 was decreased to reflect Receptacle removal on Plan E-2P.

Panel PP2, Circuit 14, Location was Mechanical Room, now Room 214.
Panel PP-2, Circuit 21, Location was Veterans Office Room 217/ 209, now Rooms 215, 216 & 218.

Panel PP-2, Circuits 22, 26 and 27 were not used.  Their location names were changed to “Spare”.
3rd Floor E-3PVAV 3-13 Circuit callout was PP3-34, now PP3-37.

One Receptacle was deleted from the West Wall of the Mechanical Room.  This was originally connected to the Ladies Restroom GFI Circuit.

One Circuit was removed from the Mens Restroom GFI Receptacle to the West Corridor Receptacle on the opposite side of the wall.  The two remaining standalone receptacles in the West Corridor were placed on Circuit 3 of Panel PP3.
E-10
Panel PP3, Circuit 2 Location was Rooms 301, 309, now Rooms 309, 317.

Panel PP3, Circuit 3, Location was Rooms 305, 309, 317, new Rooms 309, 317.

Panel PP3, Circuit 4, Location was Rooms 302, 309, now Room 309.

Panel PP3, Circuits 15 and 26- Location Description clarification only.

Panel PL3, Circuit 26, Location was Room 318, now 324.

Panel PL3, Circuit 27, Location was Room 320, now West Corridor.

Panel PL3, Circuit 29, Location was Room 312, now Room 315.

Panel PL3, Circuit 30, Location was Room 323, now Room 322.

Panel PL3, Circuit 32, Location was Room 309, now 313.

Panel PL3, Circuit 33, Location was Room 321, now Room 323.

Panel PL3, Circuit 34, Location was Room 313, now Room 309.
4th Floor
One Circuit was removed from the Mens Restroom GFI Receptacle to the West Corridor

Receptacle on the opposite side of the wall.  The remaining Receptacle was placed on Circuit 29 of Panel PP4.
E-10

Panel PP4, Circuit 6 was not used.  Its location name was changed to “Spare”.

Panel PP4, Circuit 9, Location was Rooms 416 & 417, now Rooms 406, 416 & 417.

Panel PP4, Circuit 12, Location was Rooms 405, 406 & 407, now Room 406, 407 & 417.

Panel PP4, Circuits 23 & 24- Location Description clarification only.

Panel PP4, Circuit 25, Location was Room 403 & Corridor, now Rooms 415 & 416.

Panel PL4, Circuit 24, Location was Room 415, now Room 414.
5th Floor E-5POne Circuit was removed from the Mens Restroom to Room 514.  The Receptacles in Room 514 were added to Circuit 9 of Panel PP5.
E-10
Panel PP5, Circuit 2, Location was Clerk of Court Recept., now C.O.C. Comp. Lab Recept.

Panel PP5, Circuits 7 and 11- Location Description clarification only.
Panel PP5, Circuit 6- Location Description clarification only.

Panel PP5, Circuit 9, Location was Corridor Recept, now Corridor, Room 514 Recept., due to Circuit change listed previous.

Panel PP5, Circuit 12, Location was Room 509, now Room 505.

Panel PL5, Circuit 27, Location was Room 414, now Room 502.
6th Floor E-6PWomens Restroom GFI Receptacle was changed from Panel PP6, Circuit 21 to Panel PP6, Circuit 25.


Main Restrooms Exhaust Fans- Circuit callout was PP6-17, now PP6-13.


Kevin Davis’ Restrooms Exhaust Fans- Circuit callout was PP6-24, now PP6-23.
E-11
Panel PP6, Circuit 6, Location was Mech./ Corr/ Room 606 Recept., now Corr. Room 606 Recept.


Panel PP6, Circuits 15 and 21- Location Description clarifications only.




Panel PP6, Circuit 25 was added for the Ladies Restroom GFI.




Panel PL6, Circuit 15, Location was Room 605, now Room 604.




Panel PL6, Circuit 15, Volt amps was 3000, now 7000.



Panel PL6, Circuit 17, Location was Room 603, now West Corridor.




Panel PL6, Circuit 25, Volt Amps was 8000, now 6000.



Panel PL6, Circuit 28, Location was Room 604, now East Corridor.
