The following are the responses to the Minutes of the City Inspectors Courtesy Walk Through dated 6/11/10.

1) The service location has been relocated to the ground floor and is approved.

2) The transformers are located in the mechanical room and are approved.

3) Ductwork resting on any light fixtures shall be raised to meet the requirements of the ½” clearance rule. The contractor shall address this correction.

4) Any ductwork that has a light below it shall be installed using the proper attachments for this application. Contractor shall verify with a submittal of that work. 

5) Some VAV boxes have power switches installed more than three feet from the unit. This is an acceptable due to existing conditions.

6) All emergency lighting is battery back up per the plans.

7) All emergency lighting at the stair towers shall be battery back up per the plans.

8) There is an 800 amp disconnect for this project and no shunt trip is required.

9) The MDP panel is located on the first floor and is approved. 

