DAMMON ENGINEERING, INC.

dammonengineering.com

ARCHITECTS					ENGINEERS

CONSULTING		DESIGN		STUDIES		EXPERT WITNESS

1095 Florida Ave.				   P.O. Box 2830				     985-649-5832

Slidell, LA 70458				Slidell, LA  70459			            FAX 985-641-5950

May 19, 2010

Mr. David Jones, Architect

Office of the State Fire Marshal

8181 Independence Blvd.

Baton Rouge, LA  70806

RE:	PO320959

St. Tammany Parish Administrative Complex

520 Old Spanish Trail

Dear Mr. Jones,

Please refer to the enclosed correspondence with you, regarding what was referred to on the drawings as a shaft.

When we designed the toilet exhaust for the building, we designed the exhaust to exit the building on each floor and into the atmosphere at that point.  The existing building had a convenient location for this to take place at the two rear corners, where the vents could be somewhat camouflaged by vertical dressing that would have openings between, making the arrangement still open to the atmosphere.

During design, I mislabeled this arrangement as a “chase,” which of course it is not.  Since then, I have referred to the dictionary and codes, which in every case when referring to buildings is describing a vertical shaft within a building and of course talks about not allowing fire to go from floor to floor.  It was misleading for me to have labeled it a shaft, as it is completely exterior to the building.

I am including two photos that I recently took, that show the area and I will show where the vent grills will go.

Mr. Neil Ricca, Chief of Fire Prevention in Slidell, saw the arrangement and agreed to speak with you about it, if you would like his opinion.

Again, I believe that none of this would have happened, except that we incorrectly identified this arrangement as a shaft.

I ask that you please allow that we have a standard building wall that will have a metal cover, with the toilet vents built into the wall.  We will then have vertical 2” x 6” tubes to enhance the appearance with approximately six inches between each tube for maximum air movement.

Sincerely,

_____________________________			_______________________________

Emmett G. (Pete) Dammon				Robert Wiltse

cc:		Mr. Bruce Crouch/St. Tammany Parish