Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 042000

UNIT MASONRY

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

SUMMARY

Section Includes:

Concrete masonry units (CMU's).

PRECONSTRUCTION TESTING

Testing prior to construction is required for masonry designed according to MSJC Code by either analytical method regardless of occupancy category. Note that for nonessential facilities authorities having jurisdiction may interpret this requirement to mean testing materials from the same lots or batches used for constructing Project rather than preconstruction tests, in which case field quality-control testing would be more appropriate.

Preconstruction Testing Service: Owner will engage a qualified independent testing agency to perform preconstruction testing indicated below. Retesting of materials that fail to comply with specified requirements shall be done at Contractor's expense.

Clay Masonry Unit Test: For each type of unit required, according to ASTM C 67 for compressive strength.

Concrete Masonry Unit Test: For each type of unit required, according to ASTM C 140 for compressive strength.

Delete first two subparagraphs below if mortar is specified to comply with proportion specification. Test methods cited in first subparagraph below are those referenced in ASTM C 270 for property specification.

Mortar Test (Property Specification): For each mix required, according to ASTM C 109/C 109M for compressive strength, ASTM C 1506 for water retention, and ASTM C 91 for air content.

Test method in first subparagraph below is useful for providing a baseline value to compare with results of field quality-control tests but is not appropriate for confirming compliance with compressive strength requirement of ASTM C 270 for property specification.

Mortar Test (Property Specification): For each mix required, according to ASTM C 780 for compressive strength.

Delete subparagraph below if grout is specified by proportions stated in ASTM C 476 rather than by compressive strength.

Grout Test (Compressive Strength): For each mix required, according to ASTM C 1019.

INFORMATIONAL SUBMITTALS

Usually retain first paragraph below. Material certificates are required for all masonry constructed under MSJC Code. Retain second option if required by authorities having jurisdiction or if the added assurance of quality that test reports provide is desired.

Material Certificates: For each type and size of product indicated. For masonry units include data on material properties, material test reports substantiating compliance with requirements.

Mix Designs: For each type of mortar and grout. Include description of type and proportions of ingredients.

Include test reports for mortar mixes required to comply with property specification. Test according to ASTM C 109/C 109M for compressive strength, ASTM C 1506 for water retention, and ASTM C 91 for air content.

Include test reports, according to ASTM C 1019, for grout mixes required to comply with compressive strength requirement.

QUALITY ASSURANCE

Masonry Standard: Comply with ACI 530.1/ASCE 6/TMS 602 unless modified by requirements in the Contract Documents.

Sample Panels: Build sample panels to verify selections made under sample submittals and to demonstrate aesthetic effects. Comply with requirements in Section 014000 "Quality Requirements" for mockups.

Build mock up for typical pier in approximate size.

Incorporation:  If approved by Architect, mock-up may be incorporated into as part of the completed work.

PROJECT CONDITIONS

Cold-Weather Requirements: Do not use frozen materials or materials mixed or coated with ice or frost. Do not build on frozen substrates. Remove and replace unit masonry damaged by frost or by freezing conditions. Comply with cold-weather construction requirements contained in ACI 530.1/ASCE 6/TMS 602.

Hot-Weather Requirements: Comply with hot-weather construction requirements contained in ACI 530.1/ASCE 6/TMS 602.

PRODUCTS

MASONRY UNITS, GENERAL

Defective Units: Referenced masonry unit standards may allow a certain percentage of units to contain chips, cracks, or other defects exceeding limits stated in the standard. Do not use units where such defects will be exposed in the completed Work.

See BIA Technical Notes 16B and NCMA TEK 7-3 for information on determining fire-resistance ratings of masonry walls.

Fire-Resistance Ratings: Where indicated, provide units that comply with requirements for fire-resistance ratings indicated as determined by testing according to ASTM E 119, by equivalent masonry thickness, or by other means, as acceptable to authorities having jurisdiction.

CONCRETE MASONRY UNITS

Retain "Regional Materials" Paragraph below for LEED-NC, LEED-CS, or LEED for Schools Credit MR 5; before retaining, verify availability of materials that comply.

Copy and revise first paragraph below for non-load-bearing CMUs (changing ASTM C 90 to ASTM C 129) if needed; they are not usually an inventory item and may have to be ordered in large quantities. Indicate load-bearing and non-load-bearing units on Drawings if both are specified.

CMUs: ASTM C 90.

Usually retain first subparagraph below only for masonry designed by analytical methods; delete if compressive strength specified in ASTM C 90, which is 1900 psi (13.1 MPa), is acceptable. See Evaluations.

Unit Compressive Strength: Provide units with minimum average net-area compressive strength of 2800 psi.

Retain one of three weights in subparagraph below or delete subparagraph for Contractor's option. Retain last option for default requirement if more than one weight is used. See Evaluations.

Density Classification: Normal weight.

Concrete building brick in first paragraph below is often used to adjust dimensions in CMU construction.

MORTAR AND GROUT MATERIALS

Coordinate requirements in this article with those in "Mortar and Grout Mixes" Article.

Retain "Regional Materials" Paragraph below for LEED-NC, LEED-CS, or LEED for Schools Credit MR 5; before retaining, verify availability of materials that comply.

Retain one or more of first four paragraphs below. Delete masonry cement if not allowed by "Mortar and Grout Mixes" Article. See Evaluations for discussion of masonry cement.

Portland Cement: ASTM C 150, Type I or II, except Type III may be used for cold-weather construction. Provide natural color or white cement as required to produce mortar color indicated.

Hydrated Lime: ASTM C 207, Type S.

Mix in first paragraph below allows better control of color than job-mixed, portland cement-lime mortar. If retaining, also retain last two paragraphs above.

Portland Cement-Lime Mix: Packaged blend of portland cement and hydrated lime containing no other ingredients.

Masonry Cement: ASTM C 91.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

Capital Materials Corporation; Flamingo Color Masonry Cement.

Cemex S.A.B. de C.V.; [Brikset Type N] [Kosmortar Type N] [Richmortar] [Victor Plastic Cement].

Essroc, Italcementi Group; [Brixment] [or] [Velvet].

Holcim (US) Inc.; [Mortamix Masonry Cement] [Rainbow Mortamix Custom Buff Masonry Cement] [White Mortamix Masonry Cement].

Lafarge North America Inc.; [Magnolia Masonry Cement] [Lafarge Masonry Cement] [Trinity White Masonry Cement].

Lehigh Cement Company; [Lehigh Masonry Cement] [Lehigh White Masonry Cement].

National Cement Company, Inc.; Coosa Masonry Cement.

<Insert manufacturer's name; product name or designation>.

Retain first paragraph below for colored cement or for pigments added at Project site.

Mortar Pigments: Natural and synthetic iron oxides and chromium oxides, compounded for use in mortar mixes and complying with ASTM C 979. Use only pigments with a record of satisfactory performance in masonry mortar.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

Davis Colors; True Tone Mortar Colors.

Lanxess Corporation; Bayferrox Iron Oxide Pigments.

Solomon Colors, Inc.; SGS Mortar Colors.

Laticrete.

Mixes in first paragraph below allow better control of color than job-mixed colored mortar. If retaining, also retain paragraphs above that specify materials included in the mixes retained below.

First paragraph below is an example of requirement for a concrete admixture often used in cold weather as an antifreeze. Appendix X1 in ASTM C 270 and BIA generally recommend not using admixtures unless they are known to have no adverse effects. Before approving the use of cold-weather admixtures, verify their acceptability by laboratory testing with mortar mix used.

Cold-Weather Admixture: Nonchloride, noncorrosive, accelerating admixture complying with ASTM C 494/C 494M, Type C, and recommended by manufacturer for use in masonry mortar of composition indicated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

Euclid Chemical Company (The); Accelguard 80.

Grace Construction Products, W. R. Grace & Co. - Conn.; Morset.

Sonneborn Products, BASF Aktiengesellschaft; Trimix-NCA.

Retain first paragraph below if integral water repellent is used in CMUs.

Water: Potable.

REINFORCEMENT

Retain first paragraph below for reinforcing bars in grouted cells. Revise if another grade of steel is required. Revise to specify epoxy-coated, stainless-steel, or galvanized bars if required.

Uncoated Steel Reinforcing Bars: ASTM A 615/A 615M or ASTM A 996/A 996M, Grade 60 (Grade 420).

Standard in first paragraph below includes requirements for mill-galvanized, carbon steel; hot-dip galvanized, carbon steel; and stainless steel. It is not necessary to specify these materials separately.

Masonry Joint Reinforcement, General: ASTM A 951/A 951M.

Mill-galvanized coating is not as thick as hot-dip galvanized coating. According to ASTM A 951/A 951M, mill-galvanized coating may be applied to wire before fabricating, but hot-dip galvanized coating must be applied after fabricating.

Interior Walls: Mill- galvanized, carbon steel.

Exterior Walls: Hot-dip galvanized, carbon steel.

Wire Size for Side Rods: 0.187-inch (4.76-mm) diameter.

Wire Size for Cross Rods: 0.187-inch (4.76-mm) diameter.

Retain first subparagraph below if adjustable (two-piece) type reinforcement is required.

Wire Size for Veneer Ties: 0.187-inch (4.76-mm) diameter.

Spacing of Cross Rods, Tabs, and Cross Ties: Not more than 16 inches (407 mm) o.c.

Provide in lengths of not less than 10 feet (3 m).

Masonry Joint Reinforcement for Single-Wythe Masonry: Either ladder or truss type with single pair of side rods.

Masonry Joint Reinforcement for Multiwythe Masonry:

Retain one or more of three subparagraphs below and coordinate with requirements in Part 3. More than one type may be needed; "Composite Masonry" and "Cavity Walls" articles specify types required for various applications.

Ladder type with 1 side rod at each face shell of hollow masonry units more than 4 inches (100 mm) wide, plus 1 side rod at each wythe of masonry 4 inches (100 mm) wide or less.

Tab type, either ladder or truss design, with 1 side rod at each face shell of backing wythe and with rectangular tabs sized to extend at least halfway through facing wythe but with at least 5/8-inch (16-mm) cover on outside face.

Adjustable (two-piece) type, either ladder or truss design, with one side rod at each face shell of backing wythe and with separate adjustable ties with pintle-and-eye connections having a maximum adjustment of 1-1/4 inches (32 mm). Size ties to extend at least halfway through facing wythe but with at least 5/8-inch (16-mm) cover on outside face.

Masonry Joint Reinforcement for Veneers Anchored with Seismic Masonry-Veneer Anchors: Single 0.187-inch- (4.76-mm-) diameter, hot-dip galvanized, carbon-steel continuous wire.

EMBEDDED FLASHING MATERIALS

See Evaluations for discussion of flashing materials before editing this article.

Coordinate first paragraph below with Section 076200 "Sheet Metal Flashing and Trim." Metal through-wall flashing is included in that Section.

Metal Flashing: Provide metal flashing complying with SMACNA's "Architectural Sheet Metal Manual," Section 076200 "Sheet Metal Flashing and Trim" and as follows:

Retain one or both of first two subparagraphs below for use with flexible flashing if required. See Evaluations.

Metal Drip Edge: Fabricate from stainless steel. Extend at least 3 inches (76 mm) into wall and 1/2 inch (13 mm) out from wall, with outer edge bent down 30 degrees.

Metal Sealant Stop: Fabricate from stainless steel. Extend at least 3 inches (76 mm) into wall and out to exterior face of wall. At exterior face of wall, bend metal back on itself for 3/4 inch (19 mm) and down into joint 1/4 inch (6 mm) to form a stop for retaining sealant backer rod.

Delete first paragraph below if only metal flashing is allowed. If concealed metal flashing is required at certain locations, indicate those locations on Drawings or revise paragraph.

Flexible Flashing: Use[ one of] the following unless otherwise indicated:

First subparagraph below is an example only; revise if other laminated products are required.

Copper-Laminated Flashing: 5-oz./sq. ft. (1.5-kg/sq. m) copper sheet bonded between 2 layers of glass-fiber cloth. Use only where flashing is fully concealed in masonry.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, provide one of the following:

Advanced Building Products Inc.; [Copper Fabric Flashing] [Copper Sealtite 2000].

Dayton Superior Corporation, Dur-O-Wal Division; Copper Fabric Thru-Wall Flashing.

Hohmann & Barnard, Inc.; H & B C-Fab Flashing.

Phoenix Building Products; Type FCC-Fabric Covered Copper.

Sandell Manufacturing Co., Inc.; Copper Fabric Flashing.

York Manufacturing, Inc.; Multi-Flash 500.

Some rubberized-asphalt flashing products are 0.040 inch (1.0 mm) thick; some are 0.030 inch (0.8 mm) thick; others are 0.025 inch (0.6 mm) thick. BIA recommends 0.030 inch (0.76 mm) as a minimum thickness.

Rubberized-Asphalt Flashing: Composite flashing product consisting of a pliable, adhesive rubberized-asphalt compound, bonded to a high-density, cross-laminated polyethylene film to produce an overall thickness of not less than 0.040 inch (1.02 mm).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, provide one of the following:

Advanced Building Products Inc.; Peel-N-Seal.

Carlisle Coatings & Waterproofing; CCW-705-TWF Thru-Wall Flashing.

Dayton Superior Corporation, Dur-O-Wal Division; Dur-O-Barrier Thru-Wall Flashing.

Fiberweb, Clark Hammerbeam Corp.; Aquaflash 500.

Grace Construction Products, W. R. Grace & Co. - Conn.; Perm-A-Barrier Wall Flashing.

Heckmann Building Products Inc.; No. 82 Rubberized-Asphalt Thru-Wall Flashing.

Hohmann & Barnard, Inc.; Textroflash.

W. R. Meadows, Inc.; Air-Shield Thru-Wall Flashing.

Polyguard Products, Inc.; [Polyguard 300] [Polyguard 400].

Sandell Manufacturing Co., Inc.; Sando-Seal.

Williams Products, Inc.; Everlastic MF-40.

Elastomeric Thermoplastic Flashing: Composite flashing product consisting of a polyester-reinforced ethylene interpolymer alloy.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, provide one of the following:

DuPont; Thru-Wall Flashing.

Hohmann & Barnard, Inc.; Flex-Flash.

Hyload, Inc.; Hyload Cloaked Flashing System.

Mortar Net USA, Ltd.; Total Flash.

EPDM Flashing: Sheet flashing product made from ethylene-propylene-diene terpolymer, complying with ASTM D 4637, 0.040 inch (1.0 mm) thick.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, provide one of the following:

Carlisle Coatings & Waterproofing; Pre-Kleened EPDM Thru-Wall Flashing.

Firestone Specialty Products; FlashGuard.

Heckmann Building Products Inc.; No. 81 EPDM Thru-Wall Flashing.

Hohmann & Barnard, Inc.; Epra-Max EPDM Thru-Wall Flashing.

Sandell Manufacturing Co., Inc.; EPDM Flashing.

Solder and Sealants for Sheet Metal Flashings: As specified in Section 076200 "Sheet Metal Flashing and Trim."

Adhesives, Primers, and Seam Tapes for Flashings: Flashing manufacturer's standard products or products recommended by flashing manufacturer for bonding flashing sheets to each other and to substrates.

MISCELLANEOUS MASONRY ACCESSORIES

Compressible Filler: Premolded filler strips complying with ASTM D 1056, Grade 2A1; compressible up to 35 percent; formulated from neoprene, urethane or PVC.

Preformed Control-Joint Gaskets: Made from styrene-butadiene-rubber compound, complying with ASTM D 2000, Designation M2AA-805 or PVC, complying with ASTM D 2287, Type PVC-65406 and designed to fit standard sash block and to maintain lateral stability in masonry wall; size and configuration as indicated.

Bond-Breaker Strips: Asphalt-saturated, organic roofing felt complying with ASTM D 226, Type I (No. 15 asphalt felt).

Weep/Vent Products: Use one of the following unless otherwise indicated:

Retain one or more of three subparagraphs below; delete all if open-head joints are used for weep holes and vents.

Cellular Plastic Weep/Vent: One-piece, flexible extrusion made from UV-resistant polypropylene copolymer, full height and width of head joint and depth 1/8 inch (3 mm) less than depth of outer wythe, in color selected from manufacturer's standard.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, provide one of the following:

Advanced Building Products Inc.; Mortar Maze weep vent.

Blok-Lok Limited; Cell-Vent.

Dayton Superior Corporation, Dur-O-Wal Division; Cell Vents.

Heckmann Building Products Inc.; No. 85 Cell Vent.

Hohmann & Barnard, Inc.; Quadro-Vent.

Wire-Bond; Cell Vent.

Products described in paragraph below can be used to keep weep holes clear and to keep cavity free draining. See Evaluations.

Cavity Drainage Material: Free-draining mesh, made from polymer strands that will not degrade within the wall cavity.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

Products: Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

Not all products in list below are available in all configurations described.

Advanced Building Products Inc.; [Mortar Break] [Mortar Break II].

Archovations, Inc.; CavClear Masonry Mat.

Dayton Superior Corporation, Dur-O-Wal Division; Polytite MortarStop.

Mortar Net USA, Ltd.; Mortar Net.

Usually retain subparagraph below to ensure competition in bidding. If only one configuration is used, revise subparagraph and combine it with the selected configuration.

Provide one of the following configurations:

First subparagraph below describes Mortar Net's "Mortar Net."

Strips, full-depth of cavity and 10 inches (250 mm) high, with dovetail shaped notches 7 inches (175 mm) deep.

First subparagraph below describes Advanced Building's "Mortar Break" and "Mortar Break II," respectively. Usually retain second option if cavity is 1-1/2 inches (38 mm) or larger.

Strips, not less than [3/4 inch (19 mm)] [1-1/2 inches (38 mm)] thick and 10 inches (250 mm) high, with dimpled surface designed to catch mortar droppings and prevent weep holes from clogging with mortar.

Sheets or strips full depth of cavity and installed to full height of cavity.

MASONRY CLEANERS

Verify acceptability of cleaner for cleaning masonry with pigmented mortar joints and for kinds of masonry units specified.

Proprietary Acidic Cleaner: Manufacturer's standard-strength cleaner designed for removing mortar/grout stains, efflorescence, and other new construction stains from new masonry without discoloring or damaging masonry surfaces. Use product expressly approved for intended use by cleaner manufacturer and manufacturer of masonry units being cleaned.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Diedrich Technologies, Inc.

EaCo Chem, Inc.

ProSoCo, Inc.

MORTAR AND GROUT MIXES

General: Do not use admixtures, including pigments, air-entraining agents, accelerators, retarders, water-repellent agents, antifreeze compounds, or other admixtures, unless otherwise indicated.

Do not use calcium chloride in mortar or grout.

Retain one or more of first three subparagraphs below to indicate acceptable mortar types.

Use [portland cement-lime] [or] [masonry cement] mortar unless otherwise indicated.

For exterior masonry, use [portland cement-lime] [or] [masonry cement] mortar.

For reinforced masonry, use [portland cement-lime] [or] [masonry cement] mortar.

Add cold-weather admixture (if used) at same rate for all mortar that will be exposed to view, regardless of weather conditions, to ensure that mortar color is consistent.

Preblended, Dry Mortar Mix: Furnish dry mortar ingredients in form of a preblended mix. Measure quantities by weight to ensure accurate proportions, and thoroughly blend ingredients before delivering to Project site.

Mortar for Unit Masonry: Comply with ASTM C 270, Proportion or Property Specification. Provide the following types of mortar for applications stated unless another type is indicated.

Before selecting mortar types, see Appendix X1 in ASTM C 270 and BIA Technical Notes 8A and 8B for recommendations; coordinate with requirements for masonry compressive strengths.

For masonry below grade or in contact with earth, use [Type M] [Type S].

For reinforced masonry, use Type N.

For exterior, above-grade, load-bearing and non-load-bearing walls and parapet walls; for interior load-bearing walls; for interior non-load-bearing partitions; and for other applications where another type is not indicated, use Type N.

For interior non-load-bearing partitions, Type O may be used instead of Type N.

Pigmented Mortar: Use colored cement product or select and proportion pigments with other ingredients to produce color required. Do not add pigments to colored cement products.

Retain first two subparagraphs below if retaining option in last paragraph above. Percentages in subparagraphs are for pigments containing only metallic oxides. If pigments containing carbon black are used, carbon black must be limited to 2 percent of portland cement by weight or 1 percent of masonry cement.

Pigments shall not exceed 10 percent of portland cement by weight.

Pigments shall not exceed 5 percent of masonry cement by weight.

Application: Use pigmented mortar for exposed mortar joints with the following units:

Decorative CMUs.

Pre-faced CMUs.

Concrete facing brick.

Face brick.

Hollow brick.

Glazed structural-clay facing tile.

Colored-Aggregate Mortar: Produce required mortar color by using colored aggregates and natural color or white cement as necessary to produce required mortar color.

Insert materials and proportions used for sample in first subparagraph below if known.

Mix to match Architect's sample.

Application: Use colored aggregate mortar for exposed mortar joints with the following units:

Decorative CMUs.

Pre-faced CMUs.

Concrete facing brick.

Face brick.

Hollow brick.

Glazed structural-clay facing tile.

Grout for Unit Masonry: Comply with ASTM C 476.

Use grout of type indicated or, if not otherwise indicated, of type (fine or coarse) that will comply with Table 1.15.1 in ACI 530.1/ASCE 6/TMS 602 for dimensions of grout spaces and pour height.

Proportion grout in accordance with ASTM C 476, Table 1 or paragraph 4.2.2 for specified 28-day compressive strength indicated, but not less than 2000 psi (14 MPa).

Provide grout with a slump of 8 to 11 inches (203 to 279 mm) as measured according to ASTM C 143/C 143M.

Epoxy Pointing Mortar: Mix epoxy pointing mortar to comply with mortar manufacturer's written instructions.

Application: Use epoxy pointing mortar for exposed mortar joints with the following units:

Pre-faced CMUs.

Glazed structural-clay facing tile.

EXECUTION

INSTALLATION, GENERAL

Use full-size units without cutting if possible. If cutting is required to provide a continuous pattern or to fit adjoining construction, cut units with motor-driven saws; provide clean, sharp, unchipped edges. Allow units to dry before laying unless wetting of units is specified. Install cut units with cut surfaces and, where possible, cut edges concealed.

Select and arrange units for exposed unit masonry to produce a uniform blend of colors and textures.

Retain paragraph below for high-suction brick. A simple test to determine if wetting is required consists of drawing a circle the size of a quarter on a brick and placing 20 drops of water in the circle; if water is absorbed within 1-1/2 minutes, the brick requires wetting.

Wetting of Brick: Wet brick before laying if initial rate of absorption exceeds 30 g/30 sq. in. (30 g/194 sq. cm) per minute when tested per ASTM C 67. Allow units to absorb water so they are damp but not wet at time of laying.

TOLERANCES

Dimensions and Locations of Elements:

For dimensions in cross section or elevation do not vary by more than plus 1/2 inch (12 mm) or minus 1/4 inch (6 mm).

For location of elements in plan do not vary from that indicated by more than plus or minus 1/2 inch (12 mm).

For location of elements in elevation do not vary from that indicated by more than plus or minus 1/4 inch (6 mm) in a story height or 1/2 inch (12 mm) total.

Lines and Levels:

For bed joints and top surfaces of bearing walls do not vary from level by more than 1/4 inch in 10 feet (6 mm in 3 m), or 1/2 inch (12 mm) maximum.

For conspicuous horizontal lines, such as lintels, sills, parapets, and reveals, do not vary from level by more than 1/8 inch in 10 feet (3 mm in 3 m), 1/4 inch in 20 feet (6 mm in 6 m), or 1/2 inch (12 mm) maximum.

For vertical lines and surfaces do not vary from plumb by more than 1/4 inch in 10 feet (6 mm in 3 m), 3/8 inch in 20 feet (9 mm in 6 m), or 1/2 inch (12 mm) maximum.

For conspicuous vertical lines, such as external corners, door jambs, reveals, and expansion and control joints, do not vary from plumb by more than 1/8 inch in 10 feet (3 mm in 3 m), 1/4 inch in 20 feet (6 mm in 6 m), or 1/4 inch maximum.

For lines and surfaces do not vary from straight by more than 1/4 inch in 10 feet (6 mm in 3 m), 3/8 inch in 20 feet (9 mm in 6 m), or 1/2 inch (12 mm) maximum.

Joints:

If Type FBS Rough brick or Type FBA brick is used, revise tolerances in three subparagraphs below to allow for variation in brick size. Consider restricting tolerances if Type FBX brick is used.

For bed joints, do not vary from thickness indicated by more than plus or minus 1/8 inch (3 mm), with a maximum thickness limited to 1/2 inch (12 mm).

For head and collar joints, do not vary from thickness indicated by more than plus 3/8 inch (9 mm) or minus 1/4 inch (6 mm).

For exposed head joints, do not vary from thickness indicated by more than plus or minus 1/8 inch (3 mm).

LAYING MASONRY WALLS

Lay out walls in advance for accurate spacing of surface bond patterns with uniform joint thicknesses and for accurate location of openings, movement-type joints, returns, and offsets. Avoid using less-than-half-size units, particularly at corners, jambs, and, where possible, at other locations.

Pattern is usually running bond. If other bond patterns are required, specify in first paragraph below or indicate on Drawings.

Bond Pattern for Exposed Masonry: Unless otherwise indicated, lay exposed masonry in running bond; do not use units with less than nominal 4-inch (100-mm) horizontal face dimensions at corners or jambs.

Built-in Work: As construction progresses, build in items specified in this and other Sections. Fill in solidly with masonry around built-in items.  Unless noted otherwise.

Revise first paragraph below if flexible perimeter joint or thermal break is required.

Fill space between steel frames and masonry solidly with mortar unless otherwise indicated.

Fill cores in hollow CMUs with grout 24 inches (600 mm) under bearing plates, beams, lintels, posts, and similar items unless otherwise indicated.

MORTAR BEDDING AND JOINTING

Lay hollow brick and CMUs as follows:

With face shells fully bedded in mortar and with head joints of depth equal to bed joints.

With webs fully bedded in mortar in all courses of piers, columns, and pilasters.

With webs fully bedded in mortar in grouted masonry, including starting course on footings.

With entire units, including areas under cells, fully bedded in mortar at starting course on footings where cells are not grouted.

Lay solid masonry units with completely filled bed and head joints; butter ends with sufficient mortar to fill head joints and shove into place. Do not deeply furrow bed joints or slush head joints.

Lay structural-clay tile as follows:

Lay vertical-cell units with full head joints unless otherwise indicated. Provide bed joints with full mortar coverage on face shells and webs.

Lay horizontal-cell units with full bed joints unless otherwise indicated. Keep drainage channels, if any, free of mortar. Form head joints with sufficient mortar so excess will be squeezed out as units are placed in position. Butter both sides of units to be placed, or butter one side of unit already in place and one side of unit to be placed.

Maintain joint thicknesses indicated except for minor variations required to maintain bond alignment. If not indicated, lay walls with 1/4- to 3/8-inch- (6- to 10-mm-) thick joints.

If another joint profile is used, revise first paragraph below or show on Drawings.

Tool exposed joints slightly concave when thumbprint hard, using a jointer larger than joint thickness unless otherwise indicated.

Cut joints flush for masonry walls to receive plaster or other direct-applied finishes (other than paint) unless otherwise indicated.

COMPOSITE MASONRY

Collar Joints: Solidly fill collar joints by parging face of first wythe that is laid and shoving units of other wythe into place.

Solid collar joints are required if sum of all wythes is needed to comply with height-to-thickness ratio requirements.

Corners: Provide interlocking masonry unit bond in each wythe and course at corners unless otherwise indicated.

Intersecting and Abutting Walls: Unless vertical expansion or control joints are shown at juncture, bond walls together as follows:

Retain one of three subparagraphs below and revise to suit Project. If more than one type of bonding is required, revise subparagraphs and show locations of each on Drawings.

Provide individual metal ties not more than 16 inches (406 mm) o.c.

Provide continuity with masonry joint reinforcement by using prefabricated T-shaped units.

Provide rigid metal anchors not more than[24 inches (610 mm) o.c. If used with hollow masonry units, embed ends in mortar-filled cores.

MASONRY JOINT REINFORCEMENT

General: Install entire length of longitudinal side rods in mortar with a minimum cover of 5/8 inch (16 mm) on exterior side of walls, 1/2 inch (13 mm) elsewhere. Lap reinforcement a minimum of 6 inches (150 mm).

Revise three subparagraphs below if different spacing is required; delete if shown on Drawings.

Space reinforcement not more than 16 inches (406 mm) o.c.

Space reinforcement not more than 8 inches (203 mm) o.c. in foundation walls and parapet walls.

Provide reinforcement not more than 8 inches (203 mm) above and below wall openings and extending 12 inches (305 mm) beyond openings in addition to continuous reinforcement.

Interrupt joint reinforcement at control and expansion joints unless otherwise indicated.

First paragraph below can be deleted if rigid anchors are used to bond walls at intersections.

Provide continuity at wall intersections by using prefabricated T-shaped units.

Provide continuity at corners by using prefabricated L-shaped units.

ANCHORING MASONRY TO STRUCTURAL STEEL AND CONCRETE

Anchor masonry to structural steel and concrete where masonry abuts or faces structural steel or concrete to comply with the following:

Provide an open space not less than 1 inch (25 mm) wide between masonry and structural steel or concrete unless otherwise indicated. Keep open space free of mortar and other rigid materials.

Anchor masonry with anchors embedded in masonry joints and attached to structure.

Space anchors as indicated, but not more than 24 inches (610 mm) o.c. vertically and 36 inches (915 mm) o.c. horizontally.

ANCHORING MASONRY VENEERS

Anchor masonry veneers to wall framing with masonry-veneer anchors to comply with the following requirements:

Fasten screw-attached anchors through sheathing to wall framing with metal fasteners of type indicated. Use two fasteners unless anchor design only uses one fastener.

BIA Technical Notes 28B recommends 2 inches (50 mm) of air space. Wider air spaces require closer tie spacing.

Embed tie sections in masonry joints. Provide not less than  1 1/2 inches (50 mm) of air space between back of masonry veneer and face of sheathing.

Locate anchor sections to allow maximum vertical differential movement of ties up and down.

Subparagraph below is based on the MSJC Code. Closer spacing is for adjustable two-piece anchors, wire anchors 0.148 inch (3.8 mm) in diameter, and corrugated sheet metal anchors; wider spacing is for all other anchors.

Space anchors as indicated, but not more than 16 inches (406 mm) o.c. vertically and  horizontally with not less than 1 anchor for each 2.67 sq. ft. (0.25 sq. m) of wall area. Install additional anchors within 12 inches (305 mm) of openings and at intervals, not exceeding 36 inches (914 mm), around perimeter.

FLASHING, WEEP HOLES, CAVITY DRAINAGE, AND VENTS

Retain option in first paragraph below if wall is designed on rain-screen principle with vents acting to equalize air-pressure differential between cavity and exterior. Indicate spacing of vents and blocking on Drawings. See Evaluations.

General: Install embedded flashing and weep holes in masonry at shelf angles, lintels, ledges, other obstructions to downward flow of water in wall, and where indicated. Install vents at shelf angles, ledges, and other obstructions to upward flow of air in cavities, and where indicated.

Install flashing as follows unless otherwise indicated:

Prepare masonry surfaces so they are smooth and free from projections that could puncture flashing. Where flashing is within mortar joint, place through-wall flashing on sloping bed of mortar and cover with mortar. Before covering with mortar, seal penetrations in flashing with adhesive, sealant, or tape as recommended by flashing manufacturer.

At lintels and shelf angles, extend flashing a minimum of 6 inches (150 mm) into masonry at each end. At heads and sills, extend flashing 6 inches (150 mm) at ends and turn up not less than 2 inches (50 mm) to form end dams.

Install metal drip edges beneath flexible flashing at exterior face of wall. Stop flexible flashing 1/2 inch (13 mm) back from outside face of wall and adhere flexible flashing to top of metal drip edge.

Install metal flashing termination beneath flexible flashing at exterior face of wall. Stop flexible flashing 1/2 inch (13 mm) back from outside face of wall and adhere flexible flashing to top of metal flashing termination.

Install weep holes in head joints in exterior wythes of first course of masonry immediately above embedded flashing and as follows:

Use specified weep/vent products to form weep holes.

Space weep holes 24 inches (600 mm) o.c. unless otherwise indicated.

Place cavity drainage material in cavities to comply with configuration requirements for cavity drainage material in "Miscellaneous Masonry Accessories" Article.

Retain paragraph below if wall is designed on rain-screen principle with vents acting to equalize air-pressure differential between cavity and exterior. Indicate spacing of vents and blocking on Drawings. See Evaluations.

Install vents in head joints in exterior wythes at spacing indicated. Use specified weep/vent products to form vents.

Close cavities off vertically and horizontally with blocking in manner indicated. Install through-wall flashing and weep holes above horizontal blocking.

REPAIRING, POINTING, AND CLEANING

In-Progress Cleaning: Clean unit masonry as work progresses by dry brushing to remove mortar fins and smears before tooling joints.

Final Cleaning: After mortar is thoroughly set and cured, clean exposed masonry as follows:

Test cleaning methods on sample wall panel; leave one-half of panel uncleaned for comparison purposes.

Delete first two subparagraphs below if cleaners are not specified in Part 2 or if cleaners are not allowed.

Protect surfaces from contact with cleaner.

Wet wall surfaces with water before applying cleaners; remove cleaners promptly by rinsing surfaces thoroughly with clear water.

Clean brick by bucket-and-brush hand-cleaning method described in BIA Technical Notes 20.

Retain last subparagraph above or first subparagraph below. Coordinate with products retained in Part 2. If high-pressure water cleaning or other methods are acceptable, delete or revise subparagraph below and insert applicable requirements.

Clean masonry with a proprietary acidic cleaner applied according to manufacturer's written instructions.

Clean concrete masonry by cleaning method indicated in NCMA TEK 8-2A applicable to type of stain on exposed surfaces.

MASONRY WASTE DISPOSAL

Retain first paragraph below if clean masonry waste can be used as fill in footing trenches, etc. This diverts some material from waste stream, conserving landfill space and energy required to haul waste away.

Waste Disposal as Fill Material: Dispose of clean masonry waste, including excess or soil-contaminated sand, waste mortar, and broken masonry units, by crushing and mixing with fill material as fill is placed.

Do not dispose of masonry waste as fill within 18 inches (450 mm) of finished grade.

Excess Masonry Waste: Remove excess clean masonry waste that cannot be used as fill, as described above, and other masonry waste, and legally dispose of off Owner's property.

END OF SECTION 042000