INTERNATIONAL BUILDING CODE 2006 REQUIREMENTS

RIVERINE AND COMBATANT CRAFT OPEATIONS FACILITY

BUILDING 2440 - OPERATIONS BUILDING

BUILDING 2441 – MAINTENANCE BUILDING

JOB #1986

Occupancy Classification:
Business, Group B. (Sec 304.1)

High Hazard H-1 (307.3)

Factory Industrial F-1 Moderate Hazard (Sec. 306.2)

Occupant Load: (TBL 1004.1.1)
Business / Training Areas = 100 Gross s.f. / occupant

8,759 s.f. Office = 88 occupants

Cages = 50 Gross s.f. / occupant

4,467 s.f. Locker Rm. = 90 occupants

Note: Cages (Locker Rm.) fall under the “Primary Function” definition for the major facility activity of Business / Training.

Armory = 300 Gross s.f. / occupant

1,456 s.f. Accessory Storage = 5 occupants

Maintenance Area = 100 Gross s.f. / occupant

6,641 s.f. Industrial area = 67 occupants

Total of 250 occupants

Exit Access Requirements: (Sec 1015/1016)
2 exits required for greater than 49 occupants in Business occupancy, (2 exits provided).

2 exits required for greater than 3 occupants in High Hazard occupancy, (2 exits provided).

2 exits required for greater than 49 occupants in Factory Industrial occupancy, (4 exits provided).

Exit access travel distance = 300’ sprinkled for Business (B) and Factory Industrial (F-1).

Exit access travel distance = 75’ sprinkled for High Hazard (H-1).

Allowable height and bldg. Area: (TBL 503)
B = 23,000 s.f. / 4 story allowed; this project 2 story - 6,544 s.f. First Floor, 6,682 s.f. Second Floor.

H = 7,000 s.f. / 1 story allowed; this project 1 story – 1,456 s.f.

Construction Classification: (Sec 602.2)
Type IIB

Fire Resistance Rating Requirements for Building Elements: (TBL 601)
Structural Frame = 0 hrs.

Bearing Walls (interior and exterior) = 0 hrs.

Non-Bearing Walls = 0 hrs.

Floor Construction = 0 hrs.

Roof Construction = 0 hrs.

Fire Resistance Rating Requirements for Exterior Walls: (TBL 602)
Exterior Walls with 10</=X<30 

Fire Separation Distance = 0 hr. for B and F-1.

Fire Separation Distance = 1 hr. for H.

Fire Alarm System Requirements: (Sec 907)
This Bldg. Does not require a Fire Alarm System in accordance with Section 907.2.2, 907.2.4, and 907.2.5.

A Fire Alarm and Voice Evacuation will be provided throughout the facility.

Fire Protection System Requirements: (Sec 903)
This Bldg requires a Fire Protection System in H accordance with Section 903.2.4.1.

A Fire Protection System will be provided throughout the Building.

Construction Documents: (Sec 1603)

This Bldg. shall be designed in accordance with IBC Section 1609 as a fully enclosed Bldg. using the following information:

Basic Wind Speed (3 second gusts) = 130 mph (Fig 1609)

Importance Factor: Category III Bldg., IE = 1.00, IS = 1.0, IW = 1.00 (TBL 1604.5)

Exposure B, determination of wind loads shall be in accordance with IBC Sec 1609.4

Minimum live loads shall be determined in accordance with TBL 1607.1

Ground snow loads = 5 psf (Fig. 1608.2)

Based on the survey of this property by Pittman, Glaze and Assoc., Inc. Registered Land Surveyor Walter Glaze, No. 6190, date 2.10.2008.

