LIFE SAFETY CODE 2006 REQUIREMENTS

RIVERINE AND COMBATANT CRAFT OPEATIONS FACILITY

BUILDING 2440 - OPERATIONS BUILDING

BUILDING 2441 – MAINTENANCE BUILDING

JOB #1986

Occupancy Classification:
New Business Occupancy (Chapter 38)

Multiple Occupancies (38.1.2)

Industrial or Storage Occupancy (Maintenance Building) is incidental to the predominant occupancy.

Classification of Hazard (38.1.5)

Operations Building – Ordinary Hazard

Maintenance Building - High Hazard (6.2.2.4)

Occupant Load: (Table 7.3.1.2, Occupant Load Factor)
Business / Training Areas = 100 ft. square. / person

8,759 s.f. Office = 88 persons

Cages = 100 ft. square / person

4,467 s.f. Locker Rm. = 45 persons

Armory = 100 ft. square. / person

1,456 s.f. General & High Hazard Industrial = 15 persons

Maintenance Area = 100 ft. square / person

6,641 s.f. Industrial area = 67 persons

Total of 215 occupants

Areas of Refuge (38.2.2.12)

Not required in building protected throughout by approved sprinkler system.

Number of Exits: (38.2.4)
2 exits required in Business Occupancy, (2 exits provided per floor).

2 exits required in General  & High Hazard Occupancy, (Armory), (2 exits provided).

2 exits required in General Industrial Occupancy, (Maintenance Building), (4 exits provided).

Exit access travel distance = 300’ sprinkled for Business and Industrial.

Exit access travel distance = 75’ sprinkled for High Hazard.

High Hazard Contents Areas (38.3.2.2)

Shall be protected by one hour rated construction and protected by an approved sprinkler system.

Detection, Alarm, and Communication System Requirements: (38.3.4)
This Facility requires and will be provided with a Fire Alarm System, manual and automatic initiation, and occupant notification. 

Fire Protection System Requirements: (Sec 903)
This Bldg requires a Fire Protection System in H accordance with Section 903.2.4.1.

A Fire Protection System will be provided throughout the Building.

