	DESIGN COORDINATION AND REVIEW - COMMENTS

NAVAL SPECIAL WARFARE COMMAND, SAN DIEGO, CA
	PROJECT MANAGER:

Terry Artrip, NAVFACSE

	COMMENTS BY:

Paul Mullins, Construction Mgr
	CODE:

 
	PHONE:

228-688-4715
	DATE:

17 Jun 2009

	PROJECT TITLE AND LOCATION:

MILCON P210, SOF RIVERINE & COMBATANT CRAFT OPS FACILITY (SBT-22) NASA STENNIS SPACE CENTER, MS
	TYPE OF REVIEW:  

100% Design

  

	NO.
	DWG.NO.

or

SPEC.SECT.
	COMMENTS
	A-E RESPONSE

	1
	A1.7
	SBT-22 needs to confirm doors with lites.  Size, and location as it relates to the security of the room.  I think that any room with s SIPR connection should not have a lite.  
	A-E agrees. SBT-22 desires 4”x24” lite exclusive of frame. Plans will be adjusted accordingly.

	2
	C1.0

Fire Protection Notes #1.
	The sprinkler system must be designed by a fire protection engineer, not a mechanical engineer as currently stated in this note.
	Note has been removed.

	3
	C1.4
	Confirm that top rail for fencing is not required, as currently shown.  
	Adjacent facilities have a top rail. A-E will confirm with User and provide accordingly.

	4
	C3.2
	No re-steel, or mesh, etc. in 4000 psi concrete?
	“Highway” mesh to be added at midpoint of slabs and shown in detail.

	5
	C3.3
	Confirm that each of the two (2) vehicle gates are independently operated – opening one does not open the other.  On that subject, how will vehicle close the gate after they pass through or will the compound be “open” while manned?
	Gates are independently operated with separate card readers. A detector to automatically close the gate will be provided.

	6
	C4.1
	Need to add sidewalk all around back side of Building 2442.
	Sidewalk has been added.

	7
	C6.5
	Any detail on the back-flow preventer?
	A detail has been provided.

	8
	P1.1
	Any details, etc., on the oil water separator?
	There is a cut sheet for a Zurn Z-1181 at the end of the Plumbing Section 22 00 00. Mechanical Engineer to comment.

	9
	A1.1
	What’s a “RC”?  Four (4) of them shown in Building 2441, but not shown on C/A1.5 cut.
	Fire Extinguisher in Recessed Cabinet, as noted in legend. RC has been added to Section C/A1.5.

	10
	A1.7
	Room Finish Schedule – Need to show recessed mat in Rm 116 but not in Rm 104.
	Finish Schedule will be corrected.

	11
	A1.7
	Note 7 needs to be referenced in the Room Finish Schedule for Rm 213.
	Note will be added to Schedule.

	12
	C5.1
	“Future” 12’ swing gate?  Isn’t this gate already in the contract?
	“Future” to be deleted from note.

	13
	C6.2
	Can we move the post indicator valve closer to the building?
	A-E will research and relocate if possible.

	14
	A1.3
	I don’t think we want to penetrate the 30# felt and insulation with brick ties.  Can we delete the 1" foam board and provide a vapor barrier with insulating value?  


	All references to 30# felt have been removed. Asphalt emulsion damp proofing shall be used on face of exterior CMU.

	15
	E1.1
	I’m told that it would be easier and less cost if we did not use any 1 ¼” conduit and went with 1 ½” whereever 1 ¼” is called for.
	Concur.  Contractor did actually use 1 1/2” in completed underground work.

	16
	
	
	

	17
	
	
	

	18
	
	
	

	19
	
	
	

	20
	
	
	

	21
	
	
	

	22
	
	
	

	23
	
	
	

	24
	
	
	

	25
	
	
	

	26
	
	
	

	27
	
	
	

	28
	
	
	

	29
	
	
	

	30
	
	
	

	31
	
	
	

	32
	
	
	

	33
	
	
	

	34
	
	
	

	35
	
	
	

	36
	
	
	

	37
	
	
	


