	DESIGN COORDINATION AND REVIEW - COMMENTS


	PROJECT MANAGER:

Terry Artrip, NAVFACSE

	COMMENTS BY:

URS Group, Inc.
	CODE:

 
	PHONE:

813-286-1711
	DATE:

16 November 2009

	PROJECT TITLE AND LOCATION:

MILCON P210, SOF RIVERINE & COMBATANT CRAFT OPS FACILITY

(SBT-22) STENNIS SPACE CENTER, MS
	TYPE OF REVIEW:  

Commentary on Responses to URS Final Design Submittal Comments and Resubmittal Documents

 

	NO


	DWG. NO.

or

SPEC. SECT.
	COMMENTS
	A-E RESPONSE

	
	
	CIVIL COMMENTS
	

	1
	Dwg C1.0
	Site Notes 2 – Please confirm the vertical datum.  Our discussions with Pittman, Glaze, and Associates indicated the vertical datum was NAVD 88?

Repeat Comment: Datum NAD 83 referenced by the Contractor is a horizontal datum and has nothing to do with the vertical datum.  Original comment stands.
	Topographic Surveys included in RFP indicate NAD 83.

	2
	Dwg C1.0
	Parking Lot Note 1 – In accordance with UFC 3-200-10N, Civil Engineering, all parking lot striping is to be white in color, except blue for handicap, regardless of the pavement material it is placed on (e.g. concrete, asphalt).

Repeat Comment: No change made.
	Note corrected.

	3
	Dwgs C1.1, C1.2, C1.3, C3.1, C3.2
	How are individual elements in the overall project tied down geometrically?  There are many dimensions, but it does not appear the project can be constructed from the currently provided information (e.g. location of road tie-ins to ex roads; changes in fence direction; pavement PC, PT; swale center line alignments, etc.)  Repeat Comment

Repeat Comment: No coordinates provided.
	Coordinates for Site elements have been established, and will be included in  resubmittal documents. 

	4
	Dwgs C1.1, C1.2, C1.3,

C3.3
	There is not enough geometry in the vicinity of the electric vehicular gate to locate the security fence and gate.  Repeat Comment

Repeat Comment: No coordinates provided.
	Coordinates for the gate will be provided in resubmittal documents.

	5
	Dwg C1.4, C1.5, C1.6
	Confirm the configuration of all security fencing, gates, etc. are acceptable with the User (e.g. top & bottom tension wires vs. top & bottom rails, etc.).  Currently different details call for different configurations or say “or”.  Drawings need to be consistent, definitive and not refer to specifications, as the specifications have been edited generically and do not establish the specific configuration.  Repeat comment – at review conference it was agreed this would be done, did it happen and what was outcome?

Repeat Comment: Details 2, 8 & 10 and Note 1 on C1.5 all call for bottom rails; however, Contractor indicates User wants bottom tension wires, not rails?  Please correct.
	User has selected top and bottom tension wire configuration at a recent jobsite QC meeting. Noted drawings corrected.

	9
	Dwg C2.1, C2.2, C2.3
	Provide new contours, as agreed to at the Review Conference, to demonstrate the intent of the design. We continue to be unable to evaluate the grading based on the limited information provided on the drawings, and thought the designer understood our concerns. Your new contours should tie to existing contours at the perimeter of the work limits. Contour intervals should probably be a maximum of 0.25 foot.

Repeat Comment:  No new contours (contours of grades for the proposed construction) provided as indicated.
	New contours provided as requested.

	17
	Dwg C4.1, C4.2
	Specifically what trees and shrubs are being provided on the project? Repeat Comment – usually a schedule with species, grades etc. is provided.

Repeat Comment: Shrubs still have not been identified and Legend still indicates Magnolia’s are ‘preferred’, which means something else could be provided.
	Legend indicates trees to be Magnolias which have been successful at adjacent facilities. We will coordinate with User to select Shrubs.

	24
	Dwg 6.3
	Meter Vault Detail – Detail does not indicate a 3-valve lockable bypass.  Is meter vault sized to accommodate it?

Repeat Comment: Detail still does not indicate or detail a 3-valve lockable bypass.
	The meter vault has been resized, (8' x  8') to accommodate an 8” 3-valve lockable bypass.

	30
	Spec

32 31 13.53
	Confirm with User that aluminum gates as identified in para 2.9.2 are acceptable as the RFP does not allow the use of aluminum.  Repeat Comment

Repeat Comment: Contractor states gate will be Sched 40 in the response, however, the specification still indicates very detailed information on an aluminum gate?
	Gate will be Sched 40 galvanized steel.

	31
	Spec 33 11 00
	Para 2.1.1 – Why has ductile iron pipe been deleted?  Flanged ductile iron pipe is required in above ground locations.

Repeat Comment: Ductile iron pipe has not been restored to the specification as indicated.
	Ductile iron pipe spec restored.

	33
	Spec 33 11 00
	Para 2.1.1.1.a – Delete reference to PVCO.  Repeat Comment

Repeat Comment: No change made.
	References removed.

	34
	Spec 33 11 00
	Para 2.1.1.1.c – Delete the last three sentences, as PVC fittings and PVCO are not permitted.  Repeat Comment

Repeat Comment: No change made.
	References removed.

	35
	Spec 33 11 00
	Delete paragraphs 2.1.1.3, 3.1.2.3, 3.1.2.4, 3.1.2.5, 3.1.2.6, and 3.1.2.7 in their entirety, as these materials are not permitted by the RFP.  Repeat Comment

Repeat Comment: No change made.
	Paragraphs removed.

	36
	Spec 33 11 00
	Para 2.1.2.7 – Delete all references to wet-barrel fire hydrants.  Repeat Comment

Repeat Comment: No change made.
	References removed.

	37
	Spec 33 11 00
	Para 2.1.2.9 and 2.2.2.12 – Allow only cast iron valve boxes.  Repeat Comment

Repeat Comment: No change made.
	References to pre-cast removed.

	38
	Spec 33 11 00
	Para 2.2.1.3 – Subparagraphs a., b., and c. shall require ASTM D 1785, Schedule 80 pipe in accordance with RFP Part 4 G301002 1.3.1.  Delete piping allowed by 2.2.1.3 para d., e., and f.  Repeat Comment

Repeat Comment: No change made.
	Subparagraphs a, b & c changed to reflect ASTM D 1785 Sch. 80 requirement. Subparagraphs d, e, &f deleted.

	39
	Spec 33 11 00
	Delete para 2.2.1.4, 2.2.1.5, 2.2.1.6, 2.2.1.7, and 2.2.1.8, as these materials are not permitted by the RFP.  Repeat Comment

Repeat Comment: No change made.
	Paragraphs deleted.

	40
	Spec 33 11 00
	Para 3.2.2 – Delete references to piping material not permitted for use on the project.  Repeat Comment

Repeat Comment: No change made.
	References deleted.

	41
	Spec 33 30 00
	Delete paragraphs 2.1.1, 2.1.2, 2.1.3, 3.1.2.1, 3.1.2.2, 3.1.2.3, and 3.2.2.1.b.1 in their entirety, as these materials are not permitted by the RFP.  Repeat Comment

Repeat Comment: No change made.
	Paragraphs deleted.

	42
	Spec 33 40 00
	Delete para 2.1.2, it applied to a section already deleted.  Repeat Comment

Repeat Comment: No change made.
	Paragraph deleted.

	43
	Spec 32 13 13.06
	In paragraph 2.3 the flexural strength has been changed from 650 psi to 4000 psi.  4000 is a compressive strength, while pavement is typically speced by flexural strength.  Please revise.

Repeat Comment: No change made.
	Specification revised.

	
	
	
	

	
	
	ARCHITECTURAL COMMENTS
	

	45
	Dwg T-3
	At Building Code Requirements – under Maintenance / Staging, the area (6,879 s.f.) appears to be incorrect.  Using the dimensions given, the area is somewhat less. Repeat Comment – there still appear to be discrepancies between this sheet, A 1.1 and LS.1.
	T-3 and A1.1 have been corrected to agree with LS.1, 6,879 s.f. 

	46
	Dwg LS.1
	Label wall ratings and show extent of the rated assembly.  Show occupancies of all spaces.  Repeat Comment – resolve discrepancies between T-3, A 1.1 and LS.1.
	T-3 and A1.1 have been modified to agree with LS.1.

	47
	Dwg LS.1
	Briefing 203 – a new exit door added for this submittal needs to be moved out of the moveable panel pocket. 
	Exit doors have been relocated.

	48
	Dwg LS.2
	Verify that the minimum width path of travel to exits has been provided and will remain unobstructed by trailer hitch tongues or any other portions of parked vehicles or equipment. This is a previous comment that we believe was followed through on, but we could find no discussion in documents of this or the results, please provide such.
	User provided hitch dimensions which are shown graphically with a note on A2.1. There is no obstruction when boats are parked according to design intent.

	49
	Dwg C1.0
	Sidewalk Note 4 – Sidewalks are typically sloped at a uniform grade (i.e. 1/8” per foot) not at a absolute elevation difference between sides. Please coordinate with site grading and verify accessibility code requirements are being met.
	Sidewalk Note 4 has been deleted.

	50
	Dwg A1.0
	At Exterior Envelope Notes #2 – modify “weep wicks or weep holes” to coordinate with requirements of specifications (plain open weep holes are not acceptable).  Delete weep ‘wicks’.
	Note corrected to say “open head weep joint with vent”.

	51
	Dwg A1.1
	Within Elec. Room 113, adjacent to the shower in room 108, is a nearly inaccessible dead space which could be included within the adjacent Janitor closet (110) and thereby made into useful space.  Repeat Comment
	User prefers the space layout and usefulness as shown.

	52
	Dwg A1.1
	Head 109 and Shower 108 do not meet military standards for privacy (no privacy screens provided) while there is an exceptionally large corridor space directly outside of these spaces which offers enough “excess” space to correct this situation for both rooms.  This layout should be reworked to correct the deficiency.  Repeat Comment
	A revised design was presented to and rejected by the User, A1.1 and A1.12, Pre-Final Submittal, July 22, 2009.

	53
	Dwg A1.2
	The windows in the east wall at either side of stair 215 are interior windows in a wall labeled on A1.5 as a 2 hour rated separation, but the windows have no label.  The windows are not permitted in the rated assembly as shown.  Contractor could use a rated window appropriate for a 2 hour wall or use a fusible-link fire curtain at each wall.  Repeat Comment
	Windows are indicated as rated on Schedule, Sht. A1.7.

	54
	Dwg A 1.3, A1.4, A1.5
	Provide background and derivation for u-factors and u-values indicated at the top of this sheet, as well as sheets A1.4 and A1.5.  Please direct us to where we may find the Exterior Wall Thermal Resistance Report referenced in your response to this comment.
	Thermal Wall Resistance Report is in the Calculations Package,  Section 2, page 54.

	55
	Dwg A 1.4
	Detail 5 on this page shows 30# felt over masonry with polyiso’ board over the felt.  This is not in compliance with RFP Part 4 B201002, para 1.1 Vapor Retarders.  Repeat Comment, it appears the felt has been changed to ‘asphalt emulsion dampproofing’. 
	Asphalt Emulsion Damproofing is correct.

	56
	Dwg A 1.4 Det 9, Dwg A 1.5 Det 10
	Change ‘weep joints’ to ‘weep holes’
	Prefer “OPEN HEAD WEEP JOINTS w/ VENT”.

	57
	Dwg A 1.4
	Provide 1” (min.) actual clear dimension air space at wall cavity not including insulation space in accordance with RFP Part 4 B201001, para 1.1.3.  Coordinate details on this sheet and A1.5 to comply.  This previous comment was not incorporated into Detail 10 on A 1.5.
	Detail has been revised.

	58
	Dwg A 1.5
	Section C on this sheet is showing the wall which separates building 2441 and building 2440 which is labeled as “2 HR. Rating UL Design No. U905”.  However that UL design does not accommodate unprotected openings such as the windows shown.  Coordinate these windows with the required rating for this separation assembly. Repeat Comment
	Windows are indicated as rated on Schedule, Sht. A1.7.

	59
	Dwg A 1.8, A1.9
	Gutters should be shown and called out at all locations where they occur.  Edge of roof is not consistent or coordinated for gutter locations.  More downspouts need to be shown and labeled on the left side of 3 on A 1.9.
	Downspouts have been added.

	60
	Dwg A 1.9
	Provide details of connections of stair elements.  NOTE: The response to this comment was that the stairs have been deleted by the User.  We hope this is an erroneous statement as the stairs are a part of the required egress for the building. Please confirm the stairs are to remain, and provide the requested details.  Previous response said stair details would be provided, please direct us to where they have been added.
	Stair details have been coordinated with fabricator and indicated on reviewed shop drawings, which have been added to revised CD.

	61
	Dwg A1.14
	Show downspout locations and slopes since the slopes are not the same throughout the roof.  Previous Comment – More downspouts are needed on left side in high roof area.
	Downspouts have been added.

	62
	Dwg A1.15
	Seat Protector Dispenser, Mirrors, Soap Dish, Shower Rods, Clip Board Holders are not located by dimension.  Provide all missing dimensions. Previous Comment – Horizontal dimensions are still missing.
	Horizontal dimensions have been added.

	63
	Dwg A2.1
	Locations of columns for the raised platform should be indicated and coordinated with the boats to minimize likelihood of collision damage.  Previous Comment – columns have but added, but require labeling.
	Columns have been labeled.

	64
	Dwg A2.2
	Tongue of trailer location relative to egress path is critical and appears to require that trailer be placed all the way into the space nearly against the platform columns.  Please determine exact clearance dimensions prior to review meeting so that this can be a discussion item at meeting.  Previous response to this comment was that User to provide exact dimensions for depiction on drawings – did this happen?
	User provided hitch dimensions which are shown graphically with a note on A2.1.



	65
	Dwg A2.2
	Where in submittal documents are calculations for sizing of gutters and downspouts? 
	Calculations have been added.

	66
	Dwg A2.3
	What is block ledge?  Is it the same as cast stone sill?
	Legend has been revised.

	67
	Dwg A2.8
	The raised platform must have a minimum egress width established where it is interrupted by the building columns. Based on previous response, is 2’-9 9/16” the minimum allowable exit width?
	The minimum allowable exit width is 2'- 6”.

	68
	Dwg CID-1.0, CID-2.0
	This drawing is intended to show what furniture goes where; however, there is no instruction as to what the furniture designations mean nor where any further information might be found.  The previous response to this comment refers to a cover sheet being added, please advise where this sheet is located.
	A legend has been added to Sht. CID-1.

	69
	Spec 08 36 13
	The overhead door specification is for panel type (like typical residential garage door) not the coiling doors indicated throughout the drawings.  Provide a coiling door spec’ coordinated with the drawings.  Repeat Comment – drawing sections show coiling doors, but spec and A 1.19 show sectional doors.
	Sectional doors removed from Spec. and A1.19 of the referenced specification.

	70
	Spec 08 36 13
	Note that the missile impact and cyclical wind tests (hurricane resistance) must be applied to overhead doors too. Please direct us to where the note referenced in your previous response has been added.
	Section 2.2, Doors and 2.3 Design Requirements.

	71
	Spec 08 51 13
	Complete editing of  paragraph 2.2.6.1.
	Edit completed.

	72
	Spec 09 29 00
	A statement disallowing the use of imported (Chinese) Gypsum Board should be added to this specification. Previous Comment – please direct us to where this statement has been added. Should probably be in 2.1.1.  Also please complete editing of 2.1.4.
	Statement located in 2.1.1.

	73
	Spec 13 34 19
	The specification for the metal building does not respond in detail to the RFP and appears to be a replication of the manufacturer’s standard spec’. In some places it contains language which is in conflict with and/or excludes compliance with, other specification sections.

It must respond to the specifics of the RFP.  For example Part 3 of the RFP requires response to IBC requirements for coastal hurricane prone region in F101001 para 1.1.2, and in F101001 para 1.2 requires aluminum/zinc coated steel for wall and roof panels.  These requirements are neither repeated nor addressed by this Metal Building specification.

Repeat Comment – please describe what revisions have been made. Also add IBC in 1.1.
	This Specification section is SpecsIntact as is the rest of the spec. manual.

Section 1.2.1.2, Design Loads, calls for conformation with the MBMA, MBSM, and ASCE/SEI 7-05, which includes IBC requirements applicable to the geographic region, as per F101001.

Section 2.4.2, Steel Sheet,  calls out the wall and roof panel  requirements, as per F101001.

Please note Metal Building Drawings and Calculations are a part of this package.

IBC reference added to 1.1.

	
	
	
	

	
	
	STRUCTURAL COMMENTS
	

	74
	Dwg S3.1
	Detail T, Coordinate joist mark number with plan.

Detail U, Coordinate joist mark number with plan.

Detail R, Coordinate joist mark number with plan.
	Details corrected to show 10K1 Joists.

	75
	Dwg S3.3
	Detail titled “26 Roll-up door lintel and jamb”, provide size of weld anchor stud. Is the design intent to provide hole at the bottom of U block to match weld stud spacing? If so, recommend to use regular cmu block in lieu of U block to ease construction task.
	Added note for anchor sttud size. Prefer use of U-Block to allow continuous #5 rebar, horizontal.

	76
	Dwg S4.1
	Change section DD/S2.1 to DD/S4.1.
	Section has been corrected.

	
	
	
	

	
	
	FIRE PROTECTION COMMENTS
	

	81
	Design Analysis
	Provide year of applicable codes.  Repeat comment.
	IBC - 2006

Life Safety Code - 2006

NFPA 13 - 2007

NFPA 72 - 2007



	82
	Design Analysis
	Reference to 13: 11.2.2.3.1 appears to be incorrect. Repeat Comment
	Previously addressed.  13:11.2.2.3.1 is a typographical error.  Should be 13:11.2.3.2.3.1



	83
	Design Analysis
	Verify use of schedule 10 pipe is acceptable based on corrosion testing or history.  See 4-2.3.2 of UFC 3-600-01. Repeat Comment
	Existing sprinklers systems at the site do not have a history of corrosion problems.  Corrosion testing indicates the possibility of corrosion "given adequate oxygen."  Of course, corrosion is always a possibility "given adequate oxygen."



	84
	Design Analysis
	Provide written evidence of acceptance by NAVFAC FPE that no hose allowance is acceptable. Repeat Comment
	We have a written approval memorandum dated 29 September 2009 from NAVFAC FPE Matthew Morse, included on revised CD.

	85
	Calculations
	Calculations not checked in detail.  It appears some nodes are still not properly connected. Repeat Comment
	Calculations have been revised.

	86
	Calculations
	There are calculations contained in this set that do not contain a 10% safety factor.  Written consent from the NAVFAC FPE is needed to show that this requirement can be waived. Repeat Comment from Sprinkler Submittal
	Same as #84 above.


Page 7 of 7

