SOF RIVERINE AND COMBATANT CRAFT OPERATIONS FACILITY REVIEW

BUILDINGS 2440, 2441, AND 2442

COMMENTS:

1. Provide structural “general notes” per UFC 3-300-10N, Section 3-2.1.
STRUCTURAL NOTES ADDED TO DRAWINGS.
2. Provide all applicable design criteria to the project, such as IBC 2006, UFC 1-200-1, UFC 3-300-10N, UFC 4-010-01, etc. per UFC 3-300-10N, Section 3-2.1.

DESIGN CRITERIA ADDED TO DRAWINGS.
3. Provide design live loads, snow loads, wind loads, seismic loads, etc. as required in IBC 2006, Section 1603.

LOADS ARE PROVIDED ON SHEET T-3.
4. If the foundation design is based on the recommendation of a geotechnical report, please refer to the geotechnical report (including company, date, project No. etc). Also, indicate soil bearing capacity per UFC 3-300-10N.

RFP INDICATED THAT IF THERE WERE NO CHANGES TO THE GEOTECHNICAL REPORT THAT IT DID NOT HAVE TO BE INCLUDED IN THE 100% REVIEW PACKAGE.
5. Provide W-shape steel column details including the anchor rod locations per UFC 3-300-10N, Section 2-2.10.4. Make sure the anchor rods are located within the grade beams and meet the edge distance requirements.

REFER TO SUPPLEMENTAL VP SHOP DRAWINGS.
6. Provide structural calculations for the foundation design. Refer to UFC 3-300-10N Section 3-4 for the calculation requirements.

REFER TO CALCULATIONS PACKAGE FOR FOUNDATION DESIGN.
7. Provide calculations for reinforced concrete masonry unit design. The calculation will include, but not limited to 19’-8” high of CMU wall, refer to Sections on Drawing S3.3, lintels, door jambs, and openings.

REFER TO CALCULATIONS PACKAGE FOR MASONRY DESIGN.
8. Since concrete masonry exterior enclosures are used in these buildings, provide the metal building stiffness and displacement analysis to ensure that the building displacement will not damage the masonry.

REFERED TO VARCO PRUDEN FOR RESPONSE.
9. The buildings are located in an open area. The wind load exposure category should be “C” per ASCE 7-05. The current wind loads calculation is based on the exposure “B” which results in a smaller wind pressure. Revise all the related design and calculations.

DISAGREE. EXPOSURE B / SURFACE ROUGHNESS B INCLUDES WOODED AREAS, AND WE BELIEVE THAT THE SITE MEETS THAT DEFINITION.

ALL PRELIMINARY AND 50% REVIEWED AND APPROVED 

DOCUMENTS, CALCULATIONS, ETC.  INDICATED EXPOSURE B.

EARLY START DOCUMENTS INDICATED EXPOSURE B.

10. Provide column grids on foundation plans. Refer to the column grids on architecture drawings.

COLUMN GRIDS ADDED.
11. Drawing S1.1, S1.3, and S2.1 – What is the top of floor slab elevation (16.0’) based on? Sea level? 
ELEVATIONS ARE BASED ON NAD 83’ PER SURVEY PROVIDED BY RFP. NOTED ON ALL FOUNDATION PLANS.
12. Drawing S1.1, S1.3, and S2.1 – Denote steel columns, grade beams, and slab thickness on foundation plans or provide plan notes.

ADDED NOTATION FOR STEEL COLUMNS, GRADE BEAMS AND SLAB THICKNESS TO ALL FOUNDATION PLANS.
13. Drawing S1.1 – Provide the thicknesses of recessed and raised floor slab.

DETAILS FOR THE CAGE AND RECESSED SLAB WIDTHS ARE PROVIDED ON SHEET S1.2.
14. Drawing S1.1 and S1.3 – The call outs 1/S1.1 and 3/S1.3 on the plans do not match the details (two steel columns on the plan verses one steel column in the detail).

CORRECTED.

15. Drawing S1.1 – Section cut A/S1.1 points to a wrong direction.

CORRECTED.

16. Drawing S1.2 – Section F/S1.2 shows the 8” slab. Is this right? Sections on drawing S1.1 show 7” slab in this area.

SLAB IN THIS AREA IS 7” THICK. CORRECTED DETAIL.

17. Drawing S1.4 – Denote what slope on the plan.

SLAB SLOPES FROM 16.0’ TO GREASE INTERCEPTOR ELEVATION NOTED ON PLAN (15.83’). 

18. Drawing S3.1 – At armory area framing, does the framing connect to metal building columns? If not, what is this framing lateral resistant? (lateral stability).

THE ARMORY FRAMING DOES CONNECT TO THE METAL BLDG COULMNS. SEE VP SHOP DRAWINGS FOR DETAILS.

19. Drawing S3.3 – Does the concrete masonry wall connect to the second floor? If yes, provide the connection detail.

YES THERE IS A CONNECTION TO THE SECOND FLOOR. SEE DETAIL 6 SHEET A1.4.

20. Drawing A2.8 – Required four anchors at detail 34/A2.7.

DESIGNER PREFERS TO USE 2 ANCHOR BOLTS AS SHOWN.

