	DESIGN COORDINATION AND REVIEW - COMMENTS


	PROJECT MANAGER:

Terry Artrip, NAVFACSE

	COMMENTS BY:

URS Group, Inc.
	CODE:

 
	PHONE:

813-286-1711
	DATE:

18 June 2009

	PROJECT TITLE AND LOCATION:

MILCON P210, SOF RIVERINE & COMBATANT CRAFT OPS FACILITY

(SBT-22) STENNIS SPACE CENTER, MS
	TYPE OF REVIEW:  

100% Design Submittal

 

	NO.


	DWG. NO.

or

SPEC. SECT.
	COMMENTS
	A-E RESPONSE

	
	
	CIVIL COMMENTS
	

	1
	General Civil
	Provide graphic scales on C1.1, C2.1, C3.2, C3.3, C6.1
	

	2
	General Civil
	Provide benchmarks (locations & data) being used for horizontal and vertical control.
	

	3
	Dwg C1.0
	Recommend deleting “Civil” from the title of this sheet as many of these notes are not civil related (Fire Protection and Architectural).
	

	4
	Dwgs C1.1, C1.2, C1.3
	Hazardous Material Storage pad – Delete reference to future as this pad is required by RFP Part 3 G2040.C (locker to be provided by the User).   Provide detail for this pad.
	

	5
	Dwgs C1.1, C1.2, C1.3
	What is note “Block out for future foundations required to be provided by User” mean?
	

	6
	Dwg C1.1, C1.2, C1.3
	Recommend removing silt fence line from these drawings, as it already shows up on the Drainage and SWPPP drawings.
	

	7
	Dwgs C1.1, C1.2, C1.3, C3.1, C3.2
	How are individual elements in the overall project tied down geometrically?  There are many dimensions, but it does not appear the project can be constructed from the currently provided information (e.g. location of road tie-ins to ex roads; changes in fence direction; pavement PC, PT; swale center line alignments, etc.)
	

	8
	Dwgs C1.1, C1.2, C1.3
	There is not enough geometry in the vicinity of the electric vehicular gate to locate the security fence and gate.
	

	9
	Dwgs C1.1, C1.2, C1.3
	There is a 33’ standoff indicated to the NE of Boat Storage that continues around the entire paved area – this line needs to be deleted as Boat Storage is classified as an Uninhabited Building. Provide a minimum 30’ dimension from the Boat Storage Bldg. to the security fence.
	

	10
	Dwgs C1.1, C1.2, C1.3
	Motorcycle Parking, Fuel Efficient Vehicles, and Carpool/Vanpool notes should refer to C3.4 for detail, not C3.3.
	

	11
	Dwgs C1.1, C1.2, C1.3
	Provide information (geometry, color, etc.) for parking space striping (parking lot & 30 govt spaces), motorcycle striping, and striping between handicap spaces.
	

	12
	Dwgs C1.1, C1.2, C1.3
	Dwgs A1.1 & A2.1 show bollards protecting the exterior of the buildings; however, none are identified and geometrically located on these civil plans?  (Please note 2 bollards appear to be missing from Dwg A1.1)
	

	13
	Dwgs C1.1, C1.2, C1.3
	Provide signage for the facility in accordance with RFP G204005.  (Repeat Comment)
	

	14
	Dwgs C1.1, C1.2, C1.3
	Provide stop signs where the project meets Lower Gainesville Road and Endeavor Blvd.
	

	15
	Dwg C1.2, C3.1
	Reference to bicycle rack pad needs to be revised, currently it’s indicated as N.I.C.?  Is it the intent that the pad be constructed by these drawings and the rack be provided as collateral equipment?
	

	16
	Dwg C1.2
	Are arrows shown in parking lot intended to be pavement markings?  If so, provide detail.
	

	17
	Dwg C1.2
	Will the chain link fence around the condenser affect the ability to maintain it?  It appears as though very limited space will be provided on three of its sides. 
	

	18
	Dwg C1.4
	Chain Link Security Fence Detail – Detail should refer back to C1.1 or C1.3, not C1.4.
	

	19
	Dwg C1.4, C1.5, C1.6
	Confirm the configuration of all security fencing, gates, etc. are acceptable with the User (e.g. top & bottom tension wires vs. top & bottom rails, etc.).  Currently different details call for different configurations or say “or”.  Drawings need to be consistent, definitive and not refer to specifications, as the specifications have been edited generically and do not establish the specific configuration.
	

	20
	Dwg C1.5
	Personnel Gate-2 Detail – What does the 2 in this title refer to?  It’s a little confusing, because can’t find reference to a 1 or a 2 anywhere else.
	

	21
	Dwg C2.1
	Notes 1 & 2 should probably be on the general notes sheet vs. here.  Clarify the vertical datum is NAVD 88.
	

	22
	Dwg C2.1, C2.2, C2.3
	Add a note referencing legend on C1.0
	

	23
	Dwg C2.1, C2.2, C2.3
	Provide all existing contours like in 50% Submittal.  It is not possible to determine how proposed grades meet existing grades.  From comparing previously provided contours, it appears as though new grades and existing contours may be off by several feet and nothing is provided addressing or resolving this issue.
	

	24
	Dwg C2.1, C2.2, C2.3
	Provide new contours to demonstrate the intent of the design. There are many potential grading problems that are being overlooked because contours have not been provided.  Swales typically have side slopes of 4H:1V (max.).  There are areas of proposed swale that appear to have side slopes of 1H:1V? Additionally, there are areas where swale elevations slope more than 10% longitudinally in one section and then only about 1% immediately adjacent to it?
	

	25
	Dwg C2.1, C2.2, C2.3
	The swale schedule doesn’t appear to be consistent with the actual slopes occurring with the spot elevations provided on the drawings.  Define what Slope (C) is portraying.  It’s not H:V which is typical.  If it’s V:H label as such?
	

	26
	Dwg C2.1, C2.2, C2.3
	Need spot elevations on either side of the raised sidewalk at the center of the parking lot.
	

	27
	Dwg C2.1, C2.2, C2.3
	An 8” pipe system is indicated behind the Boat Storage Bldg to, we assume, capture off-site runoff. No calculations have been provided establishing the area and volume of water that will be flowing to this system and not enough information has been provided to see how grading and end treatment at the upstream end of this pipe is to be accomplished.  An 8” pipe is not permitted by UFC 3-200-10N, as it will be subject to clogging due to debris. The smallest pipe permitted by UFC 3-200-10N is a 15”, however, the size should be determined by actual runoff conditions.  Please revise.
	

	28
	Dwg C2.1, C2.2, C2.3
	Provide grate elevations for catch basins.
	

	29
	Dwg C2.1, C2.2, C2.3
	It’s not clear what drainage area is flowing to the 18” catch basin system?  An 18” catch basin is not adequately sized for maintenance and does agree with detail on C2.4?
	

	30
	Dwg C2.1, C2.2, C2.3
	A note calls for “All building gutters to drain onto concrete”, however a portion of two roofs are shown with arrows flowing toward grass areas?  Please clarify.
	

	31
	Dwg C2.1, C2.2, C2.3
	All stormwater pipe is required to be concrete.  Please delete references to CMP.
	

	32
	Dwg C2.4
	Discharge Area Erosion Control Detail – Where is this detail being used, can’t find on C2.1?
	

	33
	Dwg C2.4
	Paved Ditch Section – Values ‘D’, ‘S’ and ‘W’ need to be defined.
	

	34
	Dwg C3.1
	Limits of curb are not clear.
	

	35
	Dwg C3.1
	Along the entrance drive to the parking lot – recommend adding a radius along the sharp edge of pavement at two locations.
	

	36
	Dwg C3.1
	Provide dimensions for handicap parking spaces and access aisle.  Handicap spaces are currently drawn at 7’ width, which is less than allowable by code.  Recommend 9’ spaces (min. req’d by RFP) separated by a 5’ access aisle.
	

	37
	Dwg C3.1
	We would suggest having smooth dowel bars in one primary direction and deformed tie bars in the other direction throughout most of the concrete pavement area.
	

	38
	Dwg C3.1, C3.2
	Define if dimensions are to face of curb or back of curb, it’s not clear.
	

	39
	Dwg C3.1, C3.2
	Suggest providing thickened edge expansion joint across concrete apron: (1) in line with end of Maintenance Bldg; (2) where Truck and Trailer Pad parking begins; and (3) where apron and roadway/drive interface.
	

	40
	Dwg C3.1, C3.2
	Provide reinforcement in irregular concrete slabs in accordance with RFP Part 3 G201003.A.
	

	41
	Dwg C3.1, C3.2
	There are several concrete slabs that indicate angular areas at joints that will crack.  Please revise to minimize cracking potential.
	

	42
	Dwg C3.2
	Details 20 thru 24 – Please provide backup documentation for derivation of diameter, length and spacing of dowel and tie bars.
	

	43
	Dwg C3.2
	It appears as though Longitudinal Joints and Transverse Joints in entrance drive plan view are labeled backwards?
	

	44
	Dwg C3.2
	Asphalt Roadway Pavement Section – Please delete the word “Roadway” in the title as this detail also applies to the parking lot.
	

	45
	Dwg C3.2
	Coordinate prime and tack coats with specification 32 12 10 and indicate all locations where they are to go (e.g. top of base course & between asphalt lifts).
	

	46
	Dwg C3.2
	The base course should extend 6” – 12” beyond the pavement edge to allow for asphalt placement and compaction.
	

	47
	Dwg C3.2
	Sidewalk Section – Provide reinforced concrete sidewalks, minimum 5” thick, in accordance with RFP Part 3 G203003.A. Be sure to identify depth of WWF.  Also recommend establishing a minimum spacing for contraction joints or refer to plan view.
	

	48
	Dwg C3.2
	Detail 30 – Correct spelling error in title.
	

	49
	Dwg C3.2
	Details 29 & 30 – Show depths for initial and secondary sawcuts.
	

	50
	Dwg C3.3
	This drawing should be referenced on C1.1.
	

	51
	Dwg C3.3
	Pedestrian gate should require 8’ fabric height, not 6’.
	

	52
	Dwg C3.3
	Ensure there is adequate space for cantilever gate to retract between roadway and sidewalk.
	

	53
	Dwg C3.3
	Define speed of Speed Limit Sign.  Coordinate with User.
	

	54
	Dwg C3.3
	Isn’t there some type of loop detector required in the pavement to automatically shut the gates once the card reader is swiped and a vehicle passes thru?
	

	55
	Dwg C3.4
	Energy Efficient Parking Sign – Recommend deleting the ‘s’ from vehicles on the sign.
	

	56
	Dwg C4.1, C4.2
	Provide specific landscaping requirements (e.g. planting materials, quantity of plantings, minimum size, etc.) Also need to provide specifications to cover these, see later comment.
	

	57
	Dwg C4.1
	Indicate grassing in the area of ‘Future Parking’.
	

	58
	Dwg C4.2
	Indicate weed fabric in details.
	

	59
	Dwg C6.1, C6.2, C6.3
	The portion of the new water line between the ex 8” main and the tee that goes to the bldg and the fire loop should be labeled as a CW (potable) line.  Change the currently indicated post indicator valve to an 8” gate valve where the new line connects to the existing main.
	

	60
	Dwg C6.1, C6.2, C6.3
	Provide an 8” post indicator valve on each fire lateral to the buildings (2 locations).  The valve should be located where the lateral connects to the fire main.
	

	61
	Dwg C6.1, C6.2, C6.3
	Please clarify that the 8” back flow preventer identified on the fire loop is a double detector check.
	

	62
	Dwg C6.1, C6.2, C6.3
	Fire Department Connections (FDC) must be withing 150 feet of a hydrant.  Ensure hydrants are between 3’ and 7’ of pavement for fire truck access.
	

	63
	Dwg C6.1, C6.2, C6.3
	Is there any need for a fire hydrant by the new parking lot that is on the unsecure side of the security fence?
	

	64
	Dwg C6.1, C6.2, C6.3
	Provide a water meter that can be read from the Facility’s EMCS in accordance with RFP Part 3 G301002.  Detail meter and show with a 3-valve lockage by-pass.
	

	65
	Dwg C6.1, C6.2, C6.3
	Note “Potential POC for Sanitary Lift Station No. 33 Invert 10.88’, See Detail Sht. C6.5”.  Has the new lift station been sized to avoid exceeding the capacity of the existing lift station? Once this is confirmed, please delete reference to ‘Potential’.  Delete reference to detail on C6.5 (the detail on C6.5 is for the new lift station adjacent to Bldg 2440, not this lift station?)  Is an invert of 10.88’ into the existing lift station correct?
	

	66
	Dwg C6.1, C6.2, C6.3
	Sanitary exiting the building is shown north of the stairs on the Plumbing Dwgs.  Please coordinate location.
	

	67
	Dwg C6.5
	Delete Sewage Disposal Trench Detail.
	

	68
	Dwg C6.5
	There are four valve/valve box details on this page, details 48, 51, 52 & 56.  Please consolidate requirements.
	

	69
	Dwg C6.5
	Lift Station Detail – Seems you might want to consider a packaged grinder pump station?
	

	70
	Dwg C6.5
	Lift Station Detail – RFP requires an adjacent valve vault to house all valves and emergency pumpout.
	

	71
	Dwg C6.5
	Lift Station Detail – Notes need to reference Lift Station Specification for requirements.
	

	72
	Dwg C6.5
	Lift Station Detail – High Level Alarm should be lower than the influent invert elevation by at least 6 inches.  Under current condition sewage will be backing up in the building lateral before maintenance can arrive.
	

	73
	Dwg C6.5
	Lift Station Detail – Vent is typically integral to the lift station unit.  Vent proposed appears prone to damage.
	

	74
	Dwg C6.5
	Lift Station Detail – What is the depth of the wet well?
	

	75
	Hydrology Study
	Calculations will need to be revised and resubmitted as a result of other comments.  Please provide design calculations for swale sizes and storm drains that take into account offsite flow thru the site.
	

	76
	Spec

03 31 00.00 10
	Para 3.10.1 Sidewalks – Add the requirement for WWF in accordance with RFP Part 3 G203003.A.
	

	77
	Spec 32 12 10
	Section needs to be edited to remove brackets.

Para 1.1 – Delete measurement and payment sections from the project.

Delineate in this spec or on the drawings where prime and tack coats are to be provided.
	

	78
	Spec

32 31 13.53
	Note 3 on Dwg C1.5 alone is not adequate for requiring green PVC coating over zinc-coated steel for all fence and gate components, as it does not work in concert with the specification. Master specification contains language relating to PVC coating, which needs to be added back into the spec in accordance with RFP Part 4 PTS G20, G202004.
	

	79
	Spec

32 31 13.53
	Confirm with User that aluminum gates as identified in para 2.9.2 are acceptable as the RFP does not allow the use of aluminum.
	

	80
	Spec 33 00 00
	Delete paragraphs 2.1.1, 2.1.2, 2.1.3, 3.1.2.1, 3.1.2.2, 3.1.2.3, and 3.2.2.1.b.1 in their entirety, as these materials are not permitted by the RFP.
	

	81
	Spec 33 11 00
	There are some random brackets throughout this section that need to be deleted before next submittal.
	

	82
	Spec 33 11 00
	Clarify where PVC and ductile iron are to be used in accordance with the RFP.  Currently there is nowhere defining this.
	

	83
	Spec 33 11 00
	Para 2.1.1.2.a – Delete reference to PVCO.
	

	84
	Spec 33 11 00
	Para 2.1.1.2.c – Delete the last three sentences, as PVC fittings and PVCO are not permitted.
	

	85
	Spec 33 11 00
	Delete paragraphs 2.1.1.3, 2.1.1.4, 2.1.1.5, 2.1.1.6, 2.1.1.7, 3.1.2.3, 3.1.2.4, 3.1.2.5, 3.1.2.6, and 3.1.2.7 in their entirety, as these materials are not permitted by the RFP.
	

	86
	Spec 33 11 00
	Para 2.1.2.7 – Delete all references to wet-barrel fire hydrants.
	

	87
	Spec 33 11 00
	Para 2.1.2.9 and 2.2.2.12 – Allow only cast iron valve boxes.
	

	88
	Spec 33 11 00
	Para 2.2.1.3 – Subparagraphs a., b., and c. shall require ASTM D 1785, Schedule 80 pipe in accordance with RFP Part 4 G301002 1.3.1.  Delete piping allowed by 2.2.1.3 para d., e., and f.
	

	89
	Spec 33 11 00
	Para 2.2.1.3 – Delete piping allowed by 2.2.1.3 para d., e., and f.  Also delete para 2.2.1.4, 2.2.1.5, 2.2.1.6, 2.2.1.7, and 2.2.1.8, as these materials are not permitted by the RFP.
	

	90
	Spec 33 11 00
	Para 3.2.2 – Delete references to piping material not permitted for use on the project.
	

	91
	Spec 33 34 00
	Delete this section as force mains are already covered under 33 30 00 Sanitary Sewers.
	

	92
	Spec 33 40 00
	Delete para 2.1.2, it applied to a section already deleted.
	

	93
	Spec 33 40 00
	Delete para 3.4.2 in its entirety as CMP is not allowed by the RFP.
	

	94
	Missing Specifications
	Provide specifications for: seed; sod; plantings; and lift station. Recommend editing 32 92 19 Seeding; 32 92 23 Sodding; 32 93 00 Exterior Plants (ensure concrete curbing and weed fabric are addressed); and 33 32 13.14 Packaged Sewage Lift Stations, Grinder Pump Type (ensure flow meters, emergency pump connection, telemetry system (Part 3 G302003.D), etc are provided in accordance with RFP.
	

	95
	Missing Specification
	In accordance with RFP Part 4 G201003, edit and submit for review Section 32 13 13.06, Portland Cement Concrete Pavement for Roads and Site Facilities.  Ensure joint sealant is provided in accordance with para 1.3.5.
	

	
	
	ARCHITECTURAL COMMENTS
	

	96
	All Dwgs
	Throughout the drawings references are made to ADA and ADAAG, these should be changed to UFAS.
	

	97
	All Dwgs
	Why are the Architectural drawings sealed by an Engineer?  They are required to be sealed by the Architect in responsible charge for the architectural design and life safety evaluation.
	

	98
	All Dwgs
	Many comments from the last review were answered with a statement that the issue would be reviewed and coordinated with one or another Engineer and/or Architect.  Please provide updated responses with the resolution of the review in such cases.  Without the resolution the comment remains open and/or unanswered.
	

	99
	All Dwgs
	Please internally review and correct drawings with poor drafting standards, especially at details.  Line weight of leaders and dimensions are often the same as object lines leading to confusion in determination of intent.  Crisscrossed leaders will lead to possible errors in reading drawings as will leader arrows inaccurately placed, or missing, and dimensions placed atop objects.
	

	100
	Dwg T-3
	At Building Code Requirements – under Maintenance / Staging, the area (6,879 s.f.) appears to be incorrect.  Using the dimensions given, the area is somewhat less. 
	

	101
	Dwg T-3
	At Building Code Requirements – under Exit Access Requirements, it is stated that 2 exits are provided for the Armory.  As they are currently arranged, they are too close together to qualify as 2 separate exits. 
	

	102
	Dwg LS.1
	Label wall ratings and show extent of the rated assembly.  Show occupancies of all spaces.  (Repeat Comment)
	

	103
	Dwg LS.1
	The Egress Capacity table should show “Required / Provided” to demonstrate Code compliance.
	

	104
	Dwg LS.1
	Briefing 203 needs 2 additional exits so that when the partition is positioned to make two separate rooms each room will have the required 2 exits.
	

	105
	Dwg LS.1
	The door for RTUO 205 must be relocated so that it will not possibly be blocked by the door to room 213 Mech / Elec.
	

	106
	Dwg LS.2
	Verify that the minimum width path of travel to exits has been provided and will remain unobstructed by trailer hitch tongues or any other portions of parked vehicles or equipment.
	

	107
	Dwg LS.2
	Provide both “Required” and “Provided” in the Egress Capacity table.
	

	108
	Dwg C1.0
	At General Notes – “Local Craftsmanship Standards” is not a recognized measure/ standard.
	

	109
	Dwg C1.0
	At fire Protection Notes – the sprinkler system must be designed by a Registered Fire Protection Engineer.
	

	110
	Dwg A1.0
	At Exterior Envelope Notes #1 – eliminate “that are sources of air leaks” and replace “caulked” with sealed.
	

	111
	Dwg A1.0
	At Exterior Envelope Notes #2 – modify “weep wicks or weep holes” to coordinate with requirements of specifications (plain open weep holes are not acceptable).
	

	112
	Dwg A1.0 
	At the Keynote Symbols legend the last two symbols are not hexagons (as labeled).
	

	113
	Dwg A1.1
	Within Elec. Room 113, adjacent to the shower in room 108, is a nearly inaccessible dead space which could be included within the adjacent Janitor closet (110) and thereby made into useful space.
	

	114
	Dwg A1.1
	Head 109 and Shower 108 do not meet military standards for privacy (no privacy screens provided) while there is an exceptionally large corridor space directly outside of these spaces which offers enough “excess” space to correct this situation for both rooms.  This layout should be reworked to correct the deficiency.
	

	115
	Dwg A1.1
	The Room Number Schedule which includes the program space requirements with the provided areas for each space displays some substantial program deviations.  Some of these have changed substantially since the last design submittal.  For example Rm. 205 RTUO went from 660/663 (sq. ft.) program/provided last submittal to 339 s.f. provided now.  This is a considerable departure from the program requirement.  The other RTUO, and the SITUO have similar disparities with the program requirements.  Please document that users are aware of and concur with these changes? 
	

	116
	Dwg A1.2
	The windows in the east wall at either side of stair 215 are interior windows in a wall labeled on A1.5 as a 2 hour rated separation, but the windows have no label.  The windows are not permitted in the rated assembly as shown.  Contractor could use a rated window appropriate for a 2 hour wall or use a fusible-link fire curtain at each wall.
	

	117
	Dwg A1.2
	The entry door to room 205 RTUO is likely to become blocked by the door into 213 Mech. / Elec.  This is not permitted by Code but could be addressed by relocating the door into room 205.
	

	118
	Dwg A 1.3, A1.4, A1.5
	Provide background and derivation for u-factors and u-values indicated at the top of this sheet, as well as sheets A1.4 and A1.5.  (Repeat Comment)
	

	119
	Dwg A 1.4
	Detail 5 on this page shows 30# felt over masonry with polyiso’ board over the felt.  This is not in compliance with RFP Part 4 B201002, para 1.1 Vapor Retarders.
	

	120
	Dwg A 1.4
	Detail 6 and 9 show the same wall assembly as detail 5 except show the 30# felt placed over the polyiso’ board rather than behind it.  These details need to be coordinated to make sure the vapor barrier is properly placed.
	

	121
	Dwg A 1.4
	Provide 1” (min.) actual clear dimension air space at wall cavity not including insulation space in accordance with RFP Part 4 B201001, para 1.1.3.  Coordinate details on this sheet and A1.5 to comply.  (Repeat Comment)
	

	122
	Dwg A 1.4
	Section B is showing the Male Shower with no ceiling.  This condition does not match the other drawings for this space – coordinate.
	

	123
	Dwg A 1.5
	Section C on this sheet is showing the wall which separates building 2441 and building 2440 which is labeled as “2 HR. Rating UL Design No. U905”.  However that UL design does not accommodate unprotected openings such as the windows shown.  Coordinate these windows with the required rating for this separation assembly.
	

	124
	Dwg A 1.5
	Show gutters at roof edges and related downspouts.
	

	125
	Dwg A 1.8, A1.9
	Gutters should be shown and called out at all locations where they occur.  Edge of roof is not consistent or coordinated for gutter locations.
	

	126
	Dwg A 1.8, A1.9
	Coordinate downspouts and related erosion control with Civil / Site design.  While splash blocks may address light rain they will easily be overcome with downpours which occur often in this area.  Site documents call for ALL downspouts to discharge onto concrete paving.  However, there is no concrete paving on two sides of these building presenting a challenge for this acceptable approach.  Splash blocks will likely create maintenance issues with erosion.
	

	127
	Dwg A 1.9
	Provide details of connections of stair elements.  NOTE: The response to this comment was that the stairs have been deleted by the User.  We hope this is an erroneous statement as the stairs are a part of the required egress for the building. Please confirm the stairs are to remain, and provide the requested details.  (Repeat Comment)
	

	128
	Dwg A1.12
	In Head 109 the grab bars are incorrectly labeled.  Though labeled differently from the last submittal, they are still incorrect.  (Repeat Comment)
	

	129
	Dwg A1.14
	Show gutters on this drawing (Roof Plan).  (Repeat Comment)
	

	130
	Dwg A1.14
	Show downspout locations and slopes since the slopes are not the same throughout the roof.
	

	131
	Dwg A1.15
	Seat Protector Dispenser, Mirrors, Soap Dish, Shower Rods, Clip Board Holders are not located by dimension.  Provide all missing dimensions.
	

	132
	Dwg A1.8, A1.19
	List doors/windows which are applicable to each elevation or otherwise tie elevations into door/window schedule.
	

	133
	Dwg A1.23
	Two details on this sheet annotate the roof as “SMR Roof Panel”.  Elsewhere the roof is noted as SSSMR, coordinate.
	

	134
	Dwg A2.1
	There should be stripes added to the floor to designate clear space required for the path of egress and this required dimension should be given on the floor plan.  Note: the tapered steel columns may play into this calculation as they project into the required space.
	

	135
	Dwg A2.1
	Boat depictions on this sheet do not match F/A2.2, which shows boats will extend under raised platform.  This appears to be a critical clearance issue/criteria. 
	

	136
	Dwg A2.1
	Locations of columns for the raised platform should be indicated and coordinated with the boats to minimize likelihood of collision damage.
	

	137
	Dwg A2.2
	Tongue of trailer location relative to egress path is critical and appears to require that trailer be placed all the way into the space nearly against the platform columns.  Please determine exact clearance dimensions prior to review meeting so that this can be a discussion item at meeting.
	

	138
	Dwg A2.2
	Vinyl faced insulation is not an acceptable finish for ceilings.  Exposed structure (painted) does not mean that vinyl faced bat insulation is an acceptable exposed finish. It is not compatible to the durability of the remainder of the building and does not comply with RFP Part 3, paragraph 2.3.5.
	

	139
	Dwg A2.2
	Indicate gutters and downspouts on building section.
	

	140
	Dwg A2.3
	Vinyl faced insulation is not an acceptable interior wall finish.  The metal panels are required to cover all interior walls at the boat storage building (see RFP Part 3 C3010 B).
	

	141
	Dwg A2.3
	There is a finish legend on this sheet which is in need of a title/label.
	

	142
	Dwg A2.3
	Where are the material designations shown in the legend used?
	

	143
	Dwg A2.8
	Detail 33 shows the raised platform railing to be constructed with removable sections but gives no indication as to how long the sections are to be.  A minimum / maximum section length should be designated and any coordination required with the parked boats stated.
	

	144
	Dwg A2.8
	The raised platform must have a minimum egress width established where it is interrupted by the building columns.
	

	145
	Dwg A2.8
	At detail 33 the centerline for the platform column is indicating an erroneous angle.
	

	146
	Dwg A2.8
	At detail 33 section mark 34 is erroneously placed at an angle to the column.
	

	147
	Dwg A2.8
	At detail H the roof is noted to be “SLR roof panel”.  Elsewhere this roof is labeled as SSSMR.
	

	148
	Dwg A2.8
	At detail H what is “3” Vinyl Faced u.f. Insulation”.
	

	149
	Dwg A2.8
	What is detail H intended to show?  It indicates no window and does not describe framing or materials around the window opening.
	

	150
	Dwg CID-1.0, CID-2.0
	This drawing is intended to show what furniture goes where; however, there is no instruction as to what the furniture designations mean nor where any further information might be found.
	

	151
	Dwg CID-1.0
	There is a note regarding power/cable locations for TVs based on model – where?  Is this a general note for all TVs?  If so it should be labeled as such. 
	

	152
	Dwg CID-2.0
	How is the “Briefing Room Option” to be applied? Direct contractor to where further information regarding this option is found.
	

	153
	Spec General
	It appears a number of the specification sections have not been edited to be project specific.  Additionally, there appear to be a number of items for which no specification sections are provided.  We suggest the designer review this matter prior to the review meeting and this be a discussion item for the meeting.
	

	154
	Spec 08 36 13
	The overhead door specification is for panel type (like typical residential garage door) not the coiling doors indicated throughout the drawings.  Provide a coiling door spec’ coordinated with the drawings.
	

	155
	Spec 08 36 13
	Note that the missile impact and cyclical wind tests (hurricane resistance) must be applied to overhead doors too.
	

	156
	Spec 08 51 13
	Anodic Coating is not an acceptable finish for the aluminum windows.  RFP Part 3 B202001, para. 1.1.1 requires factory applied high performance organic coating.
	

	157
	Spec 09 29 00
	A statement disallowing the use of imported (Chinese) Gypsum Board should be added to this specification.
	

	158
	Spec 13 34 19
	The specification for the metal building does not respond in detail to the RFP and appears to be a replication of the manufacturer’s standard spec’. In some places it contains language which is in conflict with and/or excludes compliance with, other specification sections.

It must respond to the specifics of the RFP.  For example Part 3 of the RFP requires response to IBC requirements for coastal hurricane prone region in F101001 para 1.1.2, and in F101001 para 1.2 requires aluminum/zinc coated steel for wall and roof panels.  These requirements are neither repeated nor addressed by this Metal Building specification.
	

	
	
	STRUCTURAL COMMENTS
	

	159
	Calculations
	Seismic load section indicates mapped spectral response Ss=11.8%g and S1=5.10%g which are not in accordance with UFC-3-10-01 Table C-2. Please coordinate.
	

	160
	Dwg S.10
	No general notes were provided.
	

	161
	Dwg S1.1
	Detail 1, Provide length for #5 T & B.
	

	162
	Dwg S1.1
	Is detail 3 an expansion joint? If so, the reinforcing in the longitudinal beam will cross the joint and defuse the expansion joint function. If this is just a crack control joint, recommend using saw cut detail.
	

	163
	Dwg S1.1
	Detail E indicates #4 stirrups with 180 deg hook at each end.  Recommend continuous #4                    for ease of construction.
	

	164
	Dwg S1.2
	Detail F indicates # 5 by 6” long. This length is not adequate to develop #5 rebar.  Recommend considering U or L shape rebar.
	

	165
	Dwg S1.3
	Detail M – See comment on S1.1 detail E.
	

	166
	Dwg S1.3
	Details J and L – Change reference section from A to H.
	

	167
	Dwg S1.3
	Detail 3/S1.3 – Should change to Detail 1/S1.3, there is no Detail 3 on this sheet.
	

	168
	Dwg S1.3
	Detail K refers to door sill detail. There is no such detail on this sheet. Please coordinate.
	

	169
	Dwg S2.1
	Detail P refers to door sill detail. There is no such detail on this sheet.  Please coordinate.
	

	170
	Dwg S2.1
	Is detail Q an expansion joint? If so, the reinforcing in the longitudinal beam and reinforcing around the column will cross the joint and defuse the functionality of the joint. If this is just a crack control joint, recommend using saw cut detail.
	

	171
	Dwg S2.1
	Detail Q – Change reference section from M to N.
	

	172
	Dwg S2.1
	Detail 4 – Provide length for #5 bar T & B.  Change reference section from M to N.
	

	173
	Dwg S2.2
	Provide framing detail for catwalk.
	

	174
	Dwg S3.1
	Detail S – Provide tube column to steel beam connection detail. Coordinate joist mark number with plan.  Provide reinforcing for cmu wall.
	

	175
	Dwg S3.1
	Detail T – Coordinate joist mark number with plan.  Provide metal deck to moment resistance frame connection detail.
	

	176
	Dwg S3.1
	Detail 6 – Provide diameter for wedge anchor.
	

	177
	Dwg S3.1
	Detail U – Coordinate joist mark number with plan.  Provide tube column to steel beam connection detail.
	

	178
	Dwg S3.1
	Detail V – Recommend changing anchor bolt to wedge anchor for ease of construction.  Recommend using the same size joist for the building.
	

	179
	Dwg S3.2
	Shouldn’t walls of Armory be fully grouted? If yes, please indicate on the sheet.
	

	180
	Dwg S3.3
	Details AA, X, Y, BB, and Z – Is the design intent to use a mechanical splice? If so, there is no need to specify the lap length.
	

	181
	Dwg S3.3
	Detail titled “26 Roll-up door lintel and jamb” – Recommend using regular cmu block at the top of the steel in lieu of U block to ease construction task.
	

	182
	Dwg S4.1
	Detail 7 – Provide slab thickness.
	

	183
	Shop Dwg: Anchor rod details sheet
	Note 3 states “…anchor rod and method of transferring forces from anchor rods to footing are to be determined by others”.  Sheet S1.1 states “reinforcing steel hairpin per building manufacturers requirements”. Who is responsible for anchor rod design?
	

	184
	Shop Dwg: Anchor rod details sheet
	Please provide weld sizes for column to base plate connection.
	

	185
	Shop Dwg: Anchor rod details sheet
	Please provide anchor rod detail for portal frame column.
	

	186
	Shop Dwg: Mezzanine Layout
	Does 3 inch concrete slab provide required fire rating for office area?
	

	187
	Shop Dwg: Mezzanine Layout
	Does cmu wall support the floor joist? If yes, please provide a detail.
	

	
	
	MECHANICAL COMMENTS
	

	188
	Dwg M1.0
	Exhaust Fan Schedule – Control and operation of exhaust fans is not provided.
	

	189
	Dwg M1.1
	MECH RM 114 – Why is fire damper shown in outside air duct at exterior wall?
	

	190
	Dwg M1.1
	MECH RM 114 – Recommend air conditioning mechanical room to prevent condensation on equipment.
	

	191
	Dwg M1.2
	MECH RM 213 – Recommend air conditioning mechanical room to prevent condensation on equipment.
	

	192
	Dwg M3.1
	Second Floor Mechanical Room – Fire damper should be shown in supply duct down to be consistent with fire damper shown in return duct down.
	

	193
	Dwg M3.1
	Second Floor Mechanical Room – Fire damper should be shown in supply duct down to be consistent with fire damper shown in return duct down.
	

	194
	General Mech
	No control drawings are provided that indicate all required sensors, smoke detectors, air flow monitors, dampers, valves, etc.  The specification does include a sequence of operation but does not appear to be tailored to this project.
	

	195
	General Mech
	Provide sanitary isometrics.
	

	196
	General Mech
	Enlarged plumbing plans should be shown for heads, showers, etc.  Plans as presented are hard to follow.
	

	197
	General Mech
	Need to provide typical plumbing details.
	

	198
	General Mech
	Need to provide air compressor detail and compressed air outlet details.
	

	
	
	ELECTRICAL COMMENTS
	

	199
	Dwg. E1.0
	Under Telecommunications Legend – Verify if the 4 port SIPRNet outlet should be terminated in a secure cable tray instead of a nonsecure cable tray.
	

	200
	Dwg. E1.1
	Provide TVSS for service entrance equipment (main circuit breakers from the generator side and also from the utility side) as required.
	

	201
	Dwg. E1.1
	Indicate service grounding electrode system as required.
	

	202
	Dwg. E1.5
	Key Note 7 – Indicate sub-base fuel tank volume.
	

	203
	Dwg. E3.1
	Indicate lighting controls for Male Shower 112.
	

	204
	Dwg. E3.1
	Indicate switching controls for Lobby 102.
	

	205
	Dwg. E3.1
	Verify if wall mounted sensors are best suited for the following rooms:  Cages 1051, Maintenance Area/Staging Area and Armory 107.  Maybe ceiling mounted sensor should be provided for full coverage of the areas?  Coordinate with Symbol Legend on Drawing E1.0.
	

	206
	Dwg. E3.2
	Room SITUO 208 – Ensure the wall mounted occupancy sensor has enough coverage for the entire room.  Maybe ceiling mounted sensor should be provided for full coverage of the areas? Coordinate with Symbol Legend on Drawing E1.0
	

	207
	Dwg. E3.3
	Add timer toggle switch to the Symbol Legend on Drawing E1.0.
	

	208
	Dwg. FA1.1
	The fire alarm control panel and the transmitter panel should be located inside Electrical Room 113.
	

	209
	Dwg. FA1.1
	Provide fire alarm remote annunciator.
	

	210
	Dwg. FA1.1
	Indicate strobes for Mass Notification System.
	

	211
	Dwg. FA1.4
	Provide fire alarm riser diagram as required.
	

	212
	Dwg. PH1.1
	Fixture Type “N” – Coordinate model number with Lighting Fixture Schedule on Drawing E1.0 in regards to the number of lamps.
	

	213
	Dwg. PH1.4
	Under Calculation Summary – Verify if the Avg/Min and Max/Min complies with IES standards.
	

	214
	Lightning Protection Dwg
	Submit Lightning Protection System Plans in Navy border with sheet number.  Provide counterpoise loop in accordance with RFP Part 3 D509003.
	

	215
	Dwg. General
	Provide lift station controls and telemetry system with recording equipment in accordance with RFP Part 3 G302003
	

	216
	Spec

26 05 71.00 40
	Items in Section 26 05 71.00 40 (NASA spec) should already be covered by 26 20 00 (NAVFAC spec). Please delete 26 05 71.00 40 and incorporate any items not covered into 26 20 00.
	

	217
	Spec

26 18 23.00 40
	Items in Section 26 18 23.00 40 (NASA spec) should already be covered by 26 12 19.10 (NAVFAC spec). Please delete 26 18 23.00 40 and incorporate any items not covered into 26 12 19.10.
	

	218
	Spec 26 20 00
	Delete sections that are not applicable to the project (e.g., 2.7.1.2 Aluminum Conductors; 2.12.1 Switched Duplex Receptacles; 2.12.6 Dryer Receptacles; etc.)
	

	219
	Spec 26 56 00
	Provide specifications for wood poles for the overhead distribution lines. 
	

	220
	Spec 28 31 76
	Delete 2.10.2 Project Beam Smoke Detector if not used on the project.
	

	221
	Spec 28 31 76
	Remove cut sheets for the conventional fire alarm control panel.  Provide addressable fire alarm control panel with voice evacuation system.
	

	222
	Spec 28 31 76
	Remove cut sheets for LED annunciator.  Provide LCD annunciator as submitted with the cut sheets.
	

	223
	Spec

33 71 02.00 20
	Delete 3.10.1 Terminating Aluminum Conductors if not used on the project.
	

	224
	Missing Specs
	In accordance with the RFP, edit and submit for review Sections 28 16 00.00 20 Basic Intrusion Detection Systems (IDS) and 28 20.00 20 Electronic Security System (ESS), Commercial.
	

	225
	BOD
	Under Power Distribution section, do not use aluminum conductors for secondary service entrance.
	

	226
	BOD
	Under Power Distribution section, specify the generator fuel tank for a minimum of 3 days fuel as required by the RFP.
	

	
	
	FIRE PROTECTION COMMENTS
	

	227
	Dwg FP-1
	Flow test appears to have static and residual at one location?  Flow test also appears to be quite far from the site, which cannot be confirmed by calculation submitted.
	Test was performed with flow hydrant & pressure  hydrant near dock. These were the closest hydrants.

	228
	Dwg FP-1
	Typically new underground pipe is shown as solid and existing underground pipe is shown as dashed.  The reviewer is unable to determine what is new and what is existing from the plans.
	Revised to comply

	229
	Dwg FP-1
	All plans appear to be not to scale.  Plans submitted must be to scale to confirm spacing and hydraulics information.
	SG drawings are to scale

	230
	Dwg FP-2
	No notation, location or call out for head cabinet is presented on the plans.
	Revised to comply

	231
	Dwg FP-2
	Boat storage building background is so screened reviewer cannot see what is involved here.  Structural members are not shown and coverage cannot be verified.
	Revised to comply

	232
	Dwg FP-2
	Inspectors test information needs to show a valve at an accessible level.
	Revised to comply

	233
	Dwg FP-2
	Heads under grated platform will require head guards with shields, to protect the sprinkler heads from cold soldering.
	Revised to comply

	234
	Dwg FP-2
	Plan elevations for piping don’t match clearance elevations stated on section.
	Revised to comply

	235
	Dwg FP-2
	No information is provided on plans for maximum head spacing from decking or head alignment in relation to decking.
	Revised to comply

	236
	Dwg FP-2
	No hanger locations are identified on any of the plans submitted.
	Revised to comply

	237
	Dwg FP-2
	No inspectors test detail information is provided on plans.
	Revised to comply

	238
	Dwg FP-2
	All piping must have sizing identified on plans.
	Revised to comply

	239
	Dwg FP-3
	The ½” uprights on these plans appear to be almost invisible to reviewer.
	Revised to comply

	240
	Dwg FP-3
	Without coupling and hanger notations reviewer cannot verify proper hanging arrangement.
	Revised to comply

	241
	Dwg FP-3
	There are several canopies shown on plan that exceed 4ft deep.  It must be confirmed that no storage is intended for these spaces and that construction consists of limited or non-combustible construction.
	Please provide more info – ref drawings, etc

	242
	Dwg FP-3
	There is piping represented on the plans without sizing and/or length.  All piping on plan must have size represented.
	Revised to comply

	243
	Dwg FP-3
	Riser nipples do not show up on plan.  Plan would be clearer with symbols showing rise and drops to clearly describe plan.
	Revised to comply

	244
	Dwg FP-3
	There are abbreviations shown on plan that are not defined.
	Revised to comply

	245
	Dwg FP-3
	The plans show “UH”.  Believing these are unit heaters, the heads placed in areas with unit heaters need to be protected according to NFPA 13 with respect to temperature and spacing.
	Revised to comply

	246
	Dwg FP-4
	Riser equipment legend note number 7 states electric bell without stating the size.
	Revised to comply                   Added sh FP-5 with riser

	247
	Dwg FP-4
	Section C-C the horizontal piping described as “to cages” does not appear to be accurate.
	Is correct

	248
	Dwg FP-4
	Walls on the plans are too light to review sprinkler spacing.
	Revised to comply

	249
	Dwg FP-4
	Plans state Bldg. 2441 second floor.  Plans should state Bldg. 2440 second floor.
	Revised to comply

	250
	Dwg FP-4
	Riser equipment legend note number 4 not shown on elevation.
	Revised to comply                   Added sh FP-5 with riser

	251
	Dwg FP-4
	Riser equipment legend note number 3 states 6” manifold, although placed on two different size systems.
	Revised to comply                   Added sh FP-5 with riser

	252
	Equipment Submittals
	All equipment submittal tech data sheets need to be marked up to inform specific information only to be used in this project.
	Will comply

	253
	Equipment Submittals
	Pages fourteen and eighteen of the flex head tech data are illegible.
	Will re-print

	254
	Design Analysis
	Provide year of applicable codes.
	By FPE

	255
	Design Analysis
	Reference to 13: 11.2.2.3.1 appears to be incorrect.
	By FPE

	256
	Design Analysis
	Verify use of schedule 10 pipe is acceptable based on corrosion testing or history.  See 4-2.3.2 of UFC 3-600-01.
	By FPE

	257
	Design Analysis
	Provide evidence of acceptance by NAVFAC FPE that no hose allowance is acceptable.
	By FPE

	258
	Calculations
	Calculations not checked in detail.  It appears some nodes are not properly connected.
	Will comply

	259
	Calculations
	Please verify there were not hydrants closer to the site that could have been tested.  We believe there is one.
	At time of test available drawings & info indicated the tested hydrants were the closest.


Page 16 of 16

