	DESIGN COORDINATION AND REVIEW - COMMENTS


	PROJECT MANAGER:

Terry Artrip, NAVFACSE

	COMMENTS BY:

URS Group, Inc.
	CODE:

 
	PHONE:

813-286-1711
	DATE:

3 April 2009

	PROJECT TITLE AND LOCATION:

MILCON P210, SOF RIVERINE & COMBATANT CRAFT OPS FACILITY (SBT-22) STENNIS SPACE CENTER, MS
	TYPE OF REVIEW:  

Early Start Submittal

Slab on Grade at Boat Storage Building  

	NO.
	DWG.NO.

or

SPEC.SECT.
	COMMENTS
	A-E RESPONSE

	1
	Specification General
	Specification section headers and format should be consistent.
	Will comply.

	2
	Specification General
	Are specs being edited in SpecsIntact?  If not, you cannot use automatic functions for confirming references, coordinating submittals, generating bracket reports, etc., and will need to do such manually.
	Specs are being edited in SpecsIntact.

	3
	Specification General
	A submittal register and verification of submittal approvals is needed before any construction work can proceed.
	Register was initiated 1.7.09 and will be provided.

	4
	Specification General
	We suggest a proposed specification list be generated and submitted for comment before starting any more sections related to main design.
	Current Table of Contents will be forwarded.

	5
	Specification General
	Please make sure submittal review and approval stamps and signing conventions conform to Navy standards.  Several appear in these documents and they are not consistent.
	Use of Navy standard stamps is being implemented.

	6
	Specification General
	Please coordinate construction submittals as to which are for Government, Designer of Record, or CQ Manager review.  The submittals for Government approval are those listed in 01332N along with administrative submittals listed elsewhere in the RFP Part 2 sections.
	Construction submittals will be coordinated in accordance with RFP.

	7
	Section           03 31 00.00 10
	This is not the section typically used for Navy projects.  Please consider using 03 30 00, Cast-in-Place Concrete.
	Will comply.

	8
	Section           03 31 00.00 10
	With this Spec there are references to other sections that are not included in this submittal.
	Other sections will be provided.

	9
	Concrete Mix Design
	The Designer of Record should review and approve the concrete mix design package and associated backup.
	DOR has complied with review and requested backup.

	10
	Concrete Mix Design
	Water cement ratio is not per page 6 of specification section 03 31 00.00 10.


	Mix design is being revised to conform with specification.

	11
	Concrete Mix Design
	Test records or trial mix results should be included with mix design per paragraph 1.7 of specification section 

03 31 00.00 10. 


	Records or results will be included.

	12
	Section           22 00 00
	This section does not appear to have been fully edited.  There are numerous brackets, blanks, and decision items still within the document.
	Response by Mechanical Engineer.

	13
	Section            22 00 00
	This section appears to allow many different materials for various uses.  Please edit out items as necessary to specify requirements intended for this job.
	Response by Mechanical Engineer.

	14
	Drawing S2.1
	Provide thickness and reinforcing for level landing.
	Corrected by designer, detail added on Sht. S2.1.

	15
	Drawing S2.1
	Provide slab control joint location and detail in both directions.
	Control joint location and detail added on Sht. S2.1. Note: One direction only.

	16
	Drawing S2.1
	Section 1/S2.1 shows the plan of footing at column please coordinate.
	Corrected by designer.

	17
	Drawing S2.1
	Column anchor bolts are not shown. Is metal building manufacturer responsible for the design and location of the anchor bolt? If not please provide the anchor bolt location and detail.
	Metal building manufacturer is responsible for location of anchor bolts. Design of anchor bolts has been coordinated between A-E and MBM.

	18
	Drawing S2.1
	Construction joint details and locations are not shown. Please provide construction joint details and locations.
	Contractor does not intend to use construction joints at Boat Storage Bldg. 2442.

	19
	Section           26 00 00.00 20
	Edit this section to delete paragraphs not applicable to this project, for example we think 2.7.1.2, 2.10.3, 2.12.2, 2.1.12.6 and 3.1.9.1 should be removed.
	Response by Electrical Engineer.

	20
	Drawing E4.3
	Please indicate mounting height for receptacles, we believe it is 48” AFF.
	Response by Electrical Engineer.

	21
	General
	A code analysis with accompanying drawings should be prepared for this building prior to construction being allowed to commence.
	Code analysis will be provided and is being coordinated by the DOR and DBFPE.

	22
	
	
	

	23
	
	
	

	24
	
	
	

	25
	
	
	

	26
	
	
	

	27
	
	
	

	28
	
	
	

	29
	
	
	

	30
	
	
	


C:\Documents and Settings\Robert\Local Settings\Temporary Internet Files\OLK1E\URS Comments - Early Start Boat Storage 4-3-093.doc

