PROJECT REVIEW COMMENTS	Project No. 0LA2083	Agency: USDA-APHIS Realty PM: Sylvia Cabello
Location: Kenner, LA	Building Name:
Review Phase: 50% CD Review	Date: 02/01/2011	Page 1 of 1
Reviewer: David Michael	Organization: GSA
Comm. No.	page No.	COMMENTS ARCH_x_ CIV __ STRC __ MECH ELEC _ _FIRE __ OTHER ___	RESOLUTIONS (BY A/E)
1	A202 & A201	Show pipe columns (shown only on A201) on new layout on A202. One of the columns may interfere with the sink?? Also: Show on M1 to ensure coordination w/MEP equipment/ductwork	CHANGES HAVE BEEN MADE TO A-202 TO SHOW THE LOCATIONS OF THE PIPE COLUMNS TO BE MOVED BY THE LESSOR. LOCATIONS HAVE BEEN COORDINATED WITH MEP DWGS.
2
3