DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


554 Old Spanish Trail



   




         985-649-5832

Slidell, LA 70458



              


           

FAX 985-641-5950

      March 1, 2012
     To: 
  Ms. Julie Little, Architect



               Office of State Fire Marshal



               1450 Poydras St., Suite 1500




               New Orleans, Louisiana 70112

RE:

PO411705

       
Dental Office for Dr. Jones

       
7240 Crowder Blvd.
       
New Orleans, Louisiana 70127

Dear Mrs. Little,

We have received your review letter of comments and have addressed your concerns.

1.

A) All occupancies are classified as Business.

B) Construction estimate is $240,000.00

C) 23,576 total square footage of the existing building, 4 stories. This square footage includes the rated corridors and rated stairwells as well, all the offices exit to the rated corridor. 
D) See the attached floor plan, the bottom floors have not been renovated or occupied since Hurricane Katrina.

E) See attached floor plan.

F) Type II B.

2.
No more than 2 stations shall be used at any given time for nitrous oxide.

3.
This building does not require a Fire Alarm System per section 907 of the IBC.

4.
This building does not require Fire Protection per section 903.2.2 of the IBC.

5.
The walls of the corridor are one hour rated as well with the doors and have closures. 
6.
Only one exit is required in a business type occupancy with less than 49 occupants. This

Business has 28.8 per the occupant load table 1004.1.1 of the IBC.

7.
Shall comply.

Owner Info:



Wade Verges – Ph 504-246-1562


7240 Crowder Blvd.



New Orleans, Louisiana 70127



Tenant Information:


Dr. Jones – Ph 210-542-0807


5800 Wright Rd.



New Orleans, Louisiana 70128

Sincerely,

Chuck Dammon 

