CHRISTWOOD UTILITY SPECS

I have included the utilities as I have drawn it up on the plans.

Because we will be using some of the existing equipment in the laundry there is little uniformity in the utility schedule.  In this schedule I have added 1 additional 20 pound machine, 2 30 pound washers,  and 1 45 pound stack dryer.  We would also be adding a new ironer.  Some of the original equipment is 19 years old.

Our recommendation would be to retain 2 of the 50 pound washers, the new 30 pound stack dryer and possibly the 2 75 pound dryers from the existing laundry.

None of this has been discussed yet.

Once it is decided on what direction we will take I will send all of the spec sheets.

WASHERS

(2) Continental EH020 Washers, 115 Volts, 15 amp circuit-using the existing EH020 there will be 1 pump

drain, and a new EH020 will be a gravity drain.  One ¾ inch hot and cold connection each washer

(2) Continental EH030 Washers, 208/240 Volt single Phase, 15 amp circuit.  Each will be gravity drain.

One ¾ inch hot and cold water connection for each washer.

(2) 50 pound washers (1 Dexter and 1 Huebsch) 208/240 Volt 3 Phase 20 amp circuit.  Each will be

Gravity drain.One ¾ inch hot and one ¾ inch cold for each washer.

DRYERS

- American Dryer AD333 Stack dryer (2 dryers in one) 72000 btu’s for each pocket

400 cfm’s each pocket, 115 volts 8.7 amps per pocket, 110 square inches of makeup air for unit

- Continental  CG45 x 2 Stack Dryer (2 dryers in one) 95000 btu’s for each pocket

600 cfm’s each pocket, 208/240 volts single phase 12 amps total, 216 square inches makeup air

- 75 pound dryers 175000 btu’s each dryer, 920 cfm’s per dryer, 115 volts 14 amps each dryer

IRONER

- Continental X13084, 98611 btu’s,  208/240 single phase, 6 amps,  4.5 amps exhaust connection

Gas connection ¾ inch