
SECTION 16018PRIVATE 

MOUNTING AND LOCATIONS
PART 1
GENERAL

1.1
SUMMARY


A.
Section Includes:


1.
Mounting and location of devices.

PART 2
PRODUCTS


NOT USED

PART 3
EXECUTION

3.1
MOUNTING HEIGHT


A.
Unless otherwise called for on drawings, the center line height of all new wiring devices shall comply with the schedule below if not specifically indicated on drawings.  Device mounting heights are from finished floor (or countertop) to center of device.


B.
All boxes shall be carefully plumbed, leveled, and rigidly secured so that subsequent operations of other Contractors will not cause misalignment.


C.
Schedule (General Guide)



Devices                                   Mounting

1.
Light Switches

48" above finish floor.


2.
Receptacles

18" AFF mounted vertically or as detailed on drawings.


3.
Telephone (for desk)
Match the height of receptacles.


4.
Telephone (for wall)
48" above finish floor.


5.
Disconnect Switch
48" above finish floor.



(mechanical space)



6.
Receptacles 

18" above finish floor.



(mechanical space)



7.
Panelboards and (in finished areas) terminal boxes


a.
In general, panelboards shall be centered approximately 4'-6" above floor.  However, the topmost switch or circuit breaker on panel shall not be higher than 6'-0" above floor.  If this condition exists, the panel boxes shall be lowered.


b.
When more than one panelboard or terminal box is mounted side-by-side, the boxes shall be lined up at the top.


8.
Exit Lights Ceiling mounted, or wall mounted 1'-0" above door, or as noted on drawings.


9.
Auxiliary control devices such as bells, push buttons, alarm stations, etc., shall be installed as marked on drawings or as directed by Owner.


10.
Receptacles, light switches, wire mold, etc., located above counters shall be coordinated with actual counter and backsplash height.  Typical mounting height at 6 inches above countertops unless noted otherwise.

3.2
EXECUTION


A.
The Contractor shall include any cost for layout of the location and mounting heights.

END OF SECTION

MOUNTING AND LOCATIONS

16018-1

