Size the steel structure for the tool room cage and ceiling.  The space above the tool room will be an open mezzanine used for storage.

Spacing c-channels for support of decking and storage = 16” o.c.(1.33 ft)

IBC Tbl 1607.1; Light Manufacturing shall have a minimum uniform distributed live load

wl = 125psf x 1.33 ft o.c. = 166.3 plf.

Approximate weight of c-channel = C8x11.5 = 11.5 plf.

¾” structural plywood decking = 2.3 psf x 1.33 ft o.c. = 3.1 plf

Length of c-channel between supports = 20ft

IBC Tbl 1604.3; Floor member deflection limit = l/240 = 240” / 240 = 1” max deflection

Dead loads wl = 11.5 + 3.1 = 14.6 plf

Live loads wl = 166.3 plf

LRFD = 1.2D + 1.6L = (1.2 x 14.6) + (1.6 x 166.3) = 283.6 plf on c-channel (or 23.6 pli)

The center of the c-channel, C8x11.5, deflects 1.08” with these loads.

Reactions at the end of the c-channel = 4,238.4 # (or 4.2k)

+++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++

Support the c-channels, C10x15.3, between columns at 24” o.c. = 9’ – 1” (or 9.083’ or 109”)

IBC Tbl 1604.3; Floor member deflection limit = l/240 = 109” / 240 = 0.45” max deflection

Select W6x12; I = 22.1 in4

Add 4,238.4 @ 24” o.c. and w = 12 plf (or 1.0 pli)

The center of the beam deflects .49” which is still good.

Reactions at columns = 7,675.8# at one end and 9,386.8 # at the other

++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++

Estimate the center column load @ 9,386.8 # x 2 = 18,773 # or 18.8k with a slenderness, effective length KL = (1.2) x 9.5’ = 11.4’

Select HSS 4x4x1/8” which can support a load of 41.8k with KL = 12’