554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

dammonengineering.com

info@dammonengineering.com

# Structural Re-Inspection

February 14, 2019

For:     Rick Hite

VIP Properties LLC

3009 Pontchartrain Drive

Slidell, La. 70458

Ref:    1537 Eastridge, Slidell, La.

Findings:

Due to an inspection from the City Of Slidell it was asked for clarification on the procedure of securing the existing exterior brick wall to the new exterior wall studs and how to close and seal the existing black board in place.

Recommendation:

It is recommended to use 6” masonry screws screwed through the back of the new studs and into the brick wall @ 12” O.C.  in lieu of brick ties.

It is recommended where the existing black board is missing between the brick and new studs to install foam insulation board and caulk around the edges to make a complete system seal.

Sincerely,

Brian Mistich, P.E.