554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net

September 30, 2013

For: 	Mr. David Champagne

124 Kilgore Court

Slidell, LA 70461

Re: 	La Mason Charles

3801 St. Charles Ave., Unit #301

New Orleans, La.

Determine if a 2” hole can be cut in existing 10” C-channel

w loading for existing 10” C-channel:

Lighting					1 psf

Hvac ductwork				2 psf

5/8” Sheetrock ceiling				2.8 psf

Metal decking for concrete			2.5 psf

3” concrete	floor	3/12 * 120 pcf  =	30 psf

Hardwood floor				4 psf

Each C-channel is approximately 24” o.c. so the floor area supported is approximately 24” wide x 12” along the C-channel:	42.3 psf x 2’ x1’ = 84.6 plf

Assumption : 10” C-channel weights 7 plf

Adding these together we get 84.6 plf + 7 plf = 91.6 plf along each C-channel

The DEAD LOAD from each C-channel supported by load bearing wall =

[(19.5’ / 2) + (9.5’ / 2)] x 91.6 plf = 1328.2 #/lf  (1.3k/lf)

LIVE LOAD on each C-channel @ 40 psf =

[(19.5’ / 2) + (9.5’ / 2)] x 2s.f. x 40psf = 1160 #/lf  (1.2k/lf)

LRFD Loads 	1.2 D + 1.6 L

w = [(1.3k x 1.2) + (1.2k x 1.6)]  =  3.48 k/lf

Vmax = 3.48k/lf x 19.5’/2 = 33.93k

@ 1’ from either support the shear =  V/1 = 33.93k/9.75;  V = 3.48k

@ 5.375’ from either support the shear =  V/5.375 = 33.93k/9.75;  V = 18.7k

Assume 10” C-channel Fy = 50ksi

Assume 10” C-channel tw = 0.083” thick

Available shear at any point = d * tw * Fy 	10 * .083 * 50ksi = 41.5 ksi

2” hole @ 1’ from support	Vavail = (10”-2”) *  .083 * 50ksi = 33.3k > 3.48k

2” hole @ 5.375’ from support	Vavail = (10”-2”) *  .083 * 50ksi = 33.3k > 18.7k

Recommendations:  It is highly recommended to drill holes only after 1ft of the end support and within the first and last 25% remaining of the beam. ( i.e. (19’-6 ½” – 2ft) / 4 )  It is also highly recommended to leave a 6” space horizontally between holes.

Sincerely,

Emmett G. (Pete) Dammon, P.E.