554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net

# Structural Inspection

December 4, 2012

For: 	Mr. Raymond Williams, Jr.

Subject:	Structural Inspection

200 Legendre Dr.

Slidell, LA 70458

Construction:

One and one-half-story wood-framed single family home, the structure was constructed on a conventional slab on grade then raised and supported on concrete masonry unit (CMU) walls with interior steel columns and steel beams.

Scope:

This inspection is limited to a visual inspection of the structure.  No inspection of the mechanical or electrical systems was performed.  This report is to identify the structurally compromised parts of this residence and recommend actions to remediate the structural integrity.  This report will also provide recommendations to secure this structure from the weather aliments.  This report will not include recommendations to return this structure back to a habitable residence.

History:

Mr. Williams contacted Dammon Engineering requesting an inspection of the referenced residence to determine its structural condition.  This residential structure was subjected to a fire on November 7, 2010.

Findings:

This structure is not structurally sound in its present condition.

Exterior and Roof:

- The roof over the front (west side) and left (northwest) side completely burned/collapsed.  The exterior walls in these areas are standing freely with no lateral support at the top.  The windows and doors of these areas are charred or missing.

- The front porch has been removed starting from the most northerly corner of the structure leaving approximately ?? feet on the most southerly corner of the structure.

The roof and trusses over the front porch is burned/missing.

The roof over the 1st floor towards the North West has burned/is missing, the exterior walls are standing without lateral support at the top of the wall.  Exterior windows and doors in this area of the residence are either burned or are missing.  The top double sill plate of the exterior walls in the part of the residence are charred.

The roof over the 2nd floor is burned/missing and the exterior walls facing the North West are charred and no longer able to support the remaining roof overhead.

The living room, kitchen and new bedroom addition were unaffected by the fire.  The raised concrete slab and the support columns of the residence also were not damaged.

Analysis:

The roof and the remaining trusses over the porch cannot support the existing roof over the porch and could cause an injury to person or property.

The exterior walls in the North West portion of the residence are standing unsupported at the top of the walls.  These walls must be supported to protect them from falling causing an injury to person or property.

Additional Notes

This residential structure has been identified by St. Tammany Parish as CONDEMED.  The second floor, floor/ceiling of 1st floor is tongue and groove and is remarkably not affected by the fire.

Recommendations/Conclusion:

- IMMEDIATELY:  The exterior walls must be laterally supported at the top of the walls.  Since the top plate of these walls are charred any remaining sheetrock must be removed from the interior side of these walls and lateral support added.  Where a window or doorway exist, both sides of the opening must be supported.  Remove and replace the remaining ceiling joists that are charred and the charred top sill plates with like lumber to the original construction.  In the most North West portion of the structure, where the span is from front of the structure to the rear, install new pre-engineered roof trusses supported by the front and rear exterior walls.  Install plywood panels over the damaged exterior windows and doors.

- IMMEDIATELY:  The roof over the remaining porch and also over the 2nd floor must be removed before it falls and causes damage property or person.

- The second floor can either be rebuilt or eliminated.  With either selection the walls and roof over the 2nd floor must be removed.

Summary:  The least cost of securing this structure and making minimal structural changes, is to support the exterior walls, cover the damaged exterior windows and doors, remove the roof over the affected areas and demo the 2nd floor.   Install a new roof over the structure    After the 2nd floor has been removed, a temporary shelter will need to be constructed to protect the 1st floor from the weather aliments if there is a  delay between demolition and roof construction.

Recommendations:

Sincerely,

Emmett G. (Pete) Dammon, P.E.