Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

September 20, 2007

Ms. Christi Burkart, CPM

Senior Property Manager

Equity Office Properties

RE:
Response to Plan Review 

Suite 2550, III Lakeway

Peoples Health Network
Dear Ms. Burkart,

The following responses are provided to the comments made during the plans review by Craig Clement.

Sheet A-1

Plumbing demo note should require that all plumbing piping be capped and water lines be valved.



The drawings have been revised to state: “DEMO CABINETS AND PLUMBING.  REMOVE ALL PLUMBING BACK TO RISER OR COMMON FEED.  CAP SEWER & VENT; INSTALL VALVE & CAP WATER LINES.”


Need to ensure that the sprinkler head closest to the entry door is more than 4” from the wall and that it is at least 6 feet from the next sprinkler head located in that room.



As per the drawings the contractor is to hire a licensed sprinkler system company, they will ensure that all sprinkler heads meet new code.

Sheet E-1


There are no fire alarm devices shown (although there is a note on A-1 regarding a licensed fire alarm contractor).



The E-1 drawing has been revised to show the location of fire alarm device(s), the licensed company will ensure fire alarm devices meets code.


The lighting is shown to be controlled as single point for all lamps per fixture.  Will this suite be required to comply with the split control system used in Lakeway III?  If not, the engineer may want to note the requirement to remove from the control split.



The E-1 has been revised to show a detail how each light fixture is controlled.


Sheet M-1


Thermostats are not shown for the modulines.  These locations should be dictated by the engineer.



Sheet M-1 has been revised to show thermostats that are attached to each moduline.


Thermostat is shown on a wall in an office.  Is there a supplemental cooling system or is this for perimeter system?  Based on Mechanical Note 2. is the existing to be replaced?



Since that are no AS-BUILT drawings have been provided for this suite we cannot determine what this existing thermostat is used for at this time.  


Balance CFM not provided for air devices.  It will be the contractor’s responsibility to convert provided information to CFM values for air balance purposes.



The Mechanical plan has been revised to indicate CFM for each air device.


There are no return air grilles indicated.  Based on previous experience in this building, we recommend ceiling return air grilles at a minimum in the Conference Room and over the copier in Copy/Filing.



The Mechanical drawing has been revised, return grilles have been added to both of these rooms.

Sincerely,

David Dammon

Project Manager

