NFPA 91, Standard for Exhaust Systems for Air Conveying of Vapors, Gases, Mists, and Noncombustible Particulate Solids, 2004 Edition.

4.1.9 Fire dampers shall be permitted to be installed in exhaust systems in the following situations:

(1) Where ducts pass through fire barriers.

4.1.12 Exhaust ducts passing through a fire barrier having a fire resistance rating of 2 hours or greater shall meet either of the following specifications:

(1) Wrapped or encased with listed or approved materials having a fire resistance rating equal to the fire barrier for 10ft of the duct on each side of the fire barrier including duct supports within this space.

Or

(2) Constructed of material and supports having a minimum fire resistance rating equal to the fire barrier.

4.1.13 Exhaust ducts passing through fire barriers of any fire resistance rating shall be protected by sealing the space around the duct with listed or approved fire stopping having a fire resistance rating equal to the fire resistance rating of the fire barrier.

4.3.1 Access doors shall be provided in horizontal ducts adjacent to elbows, junctions, and vertical ducts.

4.3.3 Access doors shall be of the same material and equal or greater thickness than the duct.

4.3.4 Required openings or other penetrations shall be scaled, gasketed, or tightly fitted so that conveyed material does not escape.

4.3.5 Access openings shall be sized to satisfy their intended purpose.

