Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

July 9, 2008

Mr. William Jensen

Office of State Fire Marshal

8181 Independence Blvd.

Baton Rouge, LA 70806

RE:  
P0311858


PEOPLES HEALTH NETWORK GENERATOR


3838 N CAUSWAY BLVD


METAIRIE, LA  70001-0000

Dear Mr. Jensen,

With regard to the above referenced project, Fire Marshal Inspector Tory Drenen inspected this project on 6/28/2008.  The inspector has a question about a duct that passes thru the “Cut off” Room and would like your ruling on the matter, please see attached report.  

Another tenant constructed this duct, for their generator, during the construction phase of PO311858.  This generator’s radiator air exhaust vent was installed through the new 2-hour fire rated wall and extends to the outside wall.  The radiator’s air exhaust duct vent is constructed with all seams welded, no access panels, once it enters the “Cut-off” Room; it does have one set of flanges, for dismantling the duct, before it terminates at the outside wall.  The penetration thru the 2-hour rated wall has been properly sealed.  Please see attached drawing and photos.

The construction of this ductwork, once the flanges have been welded, should be considered as having a 2-hour rating since passes thru the “Cut-off” Room without an opening. 

If you have any questions, please feel free to contact my associate David Dammon at the same number above.

Sincerely,

Emmett G. Dammon Jr.

License # 8796

