Memo to File:

November 28, 2007

Subject: Peoples Health Network Generator at Lakeway III 

Met with Hank and Alan at their office.  Discussed the following issues:

1. The generator was designed to sit its skids without the fuel tank.  The result is that the generator is now supported on only 4 points by means of legs from the skid down to the beams that were installed.

a. Since the generator is now only being supported on 2 beams, not the 5 designed to hold the generator; we discussed measures to distribute the load.

i. Install a plate across the beams for the legs to attach to.

ii. Install 3 additional legs on each side, so that each beam holds equal amounts of weight.

The option for 3 additional legs each side, was decided to be the most practical and lest expensive.

b. Since the generator is now sitting on top of the fuel cell, the generator is taller than expected.  The exhaust will not work as designed.  There is a issue with the sprinkler system water line.

c. Also, since the generator is now sitting on top of the fuel cell, how do we get fuel from the larger tank to the day tank.

i. My suggestion was to investigate the possibility of having the day tank float system activate a solenoid to start a replenishment from the larger tank.  Then de-activate the solenoid once it was ¾ full. 

David Dammon  

Dammon Engineering

