Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

October 12, 2006

Mr. Wendell LeBlanc

Equity Office

3900 North Causeway Blvd.

Suite 1350

Metairie, LA 70002-1746

RE:  
Project: Peoples Health Network Generator 

Location: 3 Lakeway

Dear Mr. LeBlanc,

PHN’s generator room was designed and approved prior to the hotel generator submittal.  Dammon Engineering was asked to review their plans for obstructions to PHN’s future generator build-out.    I need to know the Fire Marshal review number for the hotel generator so that I can provide it to Mr. William Jenson.  During this review the Fire Marshal would have instructed the hotel that they require a 2-hour separation when penetrating a 2-hour rated construction.

In order to facilitate the completion of the PHN’s generator room, I propose that a 2-hour rated fire damper be installed in the radiator exhaust plenum.  Should the damper be triggered this damper should be equipped with a grounding device to turn-off the hotel generator, to ensure the generator does not overheat.

Sincerely,

David Dammon

Project Manager

Cc: Rick Tittle

