[image: image1.png]SINA Y

b\ ~
Y

5
-
%



[image: image2.png]


DEPARTMENT OF PUBLIC SAFETY AND CORRECTIONS

[image: image3.png]SINA Y

b\ ~
Y

5
-
%



Public Safety Services


October 26, 2006

                        



315362










To: Dean Borne, Administrator

City of Slidell

1330 Bayou Lane, Suite 106

Slidell, LA 70458

Re: Mt. Olive Feeding Ministry

Second Street

Slidell, LA 70458

POR : Dammon Engineering

This review is for interior refinish and store fixture replacement, no apparent change in occupancy classification per IBC.

I Building Planning: Reviewed per the 2003 International Building Code.

       
1) Occupancy/Use Group Classification:

The proposed use of the tenant space is Assembly - Group A-2 in accordance with Section 303.1.

2) Building Limitations/Construction Type

Construction Type is indicated to be Type V (B). 

The building as proposed appears to comply with the height and area limits of Table 503, of the use and construction type.

3) Special Occupancy Areas 

There are no special use areas indicated.

II Fire Protection Systems: Reviewed per the 2003 International Building Code.

1) Fire Resistant Materials and Construction

There is no new fire resistant rated construction indicated.

2) Interior Finishes

Rooms and enclosed spaces are permitted to have minimum Class B interior finish materials at walls and ceilings per Table 803.5.

3) Fire Protection Systems

The building is not provided with an automatic sprinkler system.

The building is not provided with a fire alarm system.

III Occupants: Reviewed per the 2003 International Building Code.

1) Means of Egress

October 26, 2006

                        



315362
1008.1.6  Thresholds at doorways shall not exceed 0.5. Raised thresholds and floor level changes greater than 0.25 inch at doorways shall be beveled with a slope not greater than one unit vertical in two units horizontal (50-percent slope). The 4” level change indicated at loading dock does not comply.

1012.1  Guards shall be located along open-sided walking surfaces, mezzanines, industrial equipment platforms, stairways, ramps and landings which are located more than 30 inches above the floor or grade below. Provide Guardrails compliant with this section at the open side of ramp and upper entry landing, and at rear landing and steps above 30” above grade.

1008.1.9  Each door in a means of egress from an occupancy of Group

A or E having an occupant load of 100 or more shall not be provided with

a latch or lock unless it is panic hardware or fire exit hardware. Provide panic hardware at proposed doors marked 100.

2) Accessibility

Refer to State Fire Marshal review P0315362 for accessibility review.  

IV Structural: Per the 2003 International Building Code.

Submittal appears to comply with the requirements of Chapter 1604 and 1609.

No flood zone is indicated in the submittal and applicability and compliance with Chapter 1612 could not be determined.

V Electrical Systems: Per the 2002 National Electrical Code, NFPA 70.
Appears to comply.

VI Mechanical Systems: Per the 2003 International Mechanical Code. 

Appears to comply.

VII Plumbing Systems: Per 2000 Louisiana State Plumbing Code

Appears to comply with required fixtures from Table 407 

October 26, 2006

                        



315362
Submit plans for review to the following:

DHH Metro Region I

Phil Jefferson

111 N. Causeway Blvd

Metarie, LA 70001

Louisiana State Fire Marshal’s office reviewed this project for the requirements of the Louisiana State Uniform Construction Code. 

This review is performed at the request of the City of Slidell La.

This review shall not constitute or be construed as a warranty or guarantee by the Office of the State Fire Marshal as to durability or fitness, or as a warranty or guarantee by the Office of the State Fire Marshal that this building, or any material, equipment, method or type of construction used therein is or will be free from defects, will perform in a particular manner, is fit for a particular purpose, or will last in any particular way.

This review shall in no way permit and/or authorize any omissions or deviations 

of specific requirements of the adopted codes, rules and regulations.

This office will not be responsible for field inspections to assure workmanship that is in accordance with this review.

Review fee:

Occupancy: A-2

Area: 4000 sq ft

Fee: $120.00

Reviewed by:

James A Waite

Staff Architect

Office of the State Fire Marshal

PAGE  
3
"Is Yours Working"??

Smoke Detectors Save Lives!!

OFFICE OF STATE FIRE MARSHAL, CODE ENFORCEMENT, AND BUILDING SAFETY

8181 INDEPENDENCE BOULEVARD, BATON ROUGE, LA 70806

(225) 925-4911     1-800-256-5452


[image: image4.png]


_1081333936.bin

_1081333981.bin

