STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana  70806
225-925-4920

V. J. BELLA
STATE FIRE MARSHAL

RENOVATION

EMMETT DAMMON
DAMMON ENGINEERING
1095 FLORIDA AVE
SLIDELL, LA  70458-0000	
RE:  P0282271
QUIZNOS  SUB  SHOP #7362
4401 AIRLINE DR
METAIRIE, LA  70001-0000

NFPA 101, 2003

ASSEMBLY 300 OCCUPANTS OR LESS

Dear Applicant:

This is to advise that we have reviewed the drawings and specifications for the subject proposed construction and have determined that they appear to satisfactorily comply with the adopted laws, codes, rules and regulations of The State Fire Marshal subject to the following requirements:

NOTE:  THE COMMENTS LISTED BELOW IDENTIFY APPARENT DEFICIENCIES DETECTED IN OUR REVIEW OF THE DOCUMENTS SUBMITTED.

1.	101:4.6.11  Buildings or portions of buildings shall be permitted to be occupied during construction, repair, alterations, or additions only if all means of egress and all fire protection features are in place and continuously maintained for the portion occupied. 

2.	LRS 40:1731-(Effective 8/15/95)  Provide handicapped accessibility in accordance with ADA-AG (Accessibility Guidelines - September 1994).  This does not include a review for compliance with the Federal Americans with Disabilities (Civil Rights) Act of 1990.  Compliance with state regulations and requirements does not guarantee compliance with federal law.  Particular deficiencies and paragraph references are noted as follows:

	a)  4.13.9  Door hardware shall comply with this section. Hardware shall not require tight grasping, tight pinching, or twisting of the wrist to operate.

	b)  4.1.3(11) and 4.1.6(3)(e)  ALL public and common use toilet rooms shall comply with requirements of this Section 4.22. 
	
3.	101:7.2.1.3  Provide landings outside exterior doors level with the interior finish floor. 

4.	101:7.2.1.5.9  Doors shall be openable with ONLY one releasing operation.  A two-step release, such as a knob and an independent slide bolt, is NOT acceptable. 

5.	HVAC system shall be constructed in accordance with 101:9.2. 

6.	RS 23:536  Boilers, Pressure Vessels, and water heaters shall conform with the provisions of the Louisiana Boiler Inspection Law in accordance with adopted rules and regulations.  (Contact our Boiler Section ( 800-256-5452 ) with any questions concerning this requirement.) 

7.	Inadequate electrical systems have been found to be a major cause of fires throughout the state.  The "Professional of Record" (Architect/Engineer) if required by LRS 37:155, otherwise, the Owner shall comply with the 2002 NFPA 70, National Electrical Code, for all proposed electrical work in this submittal.  Electrical work/modifications may include, but not limited to the following: lighting fixtures (interior, exterior and site); receptacles; panelboards; panel schedules; load schedules; utility company or service transformer KVA size, number of phases, voltage and secondary short circuit amps; fixture schedules; wire type, size and circuiting; single line diagram; properly sized new and existing protective equipment, including service disconnect(s), panelboard(s), circuit breakers and fused switches, sized for available short circuit amps; properly sized system grounding conductor and grounding electrode(s); connection of the system grounding and bonding at the service disconnect enclosure(s); properly sized overload or overcurrent and short circuit protective devices for conductors, motors, transformers and equipment; properly sized conductors for equipment grounding and bonding of all metallic conduit and enclosures; installation of ground fault circuit receptacles; etc. 

8.	NOTE: Please enclose a copy of this letter with future submittals or other correspondence pertaining to this project. 

Changes to construction in the field which are not consistent with the reviewed documents are not authorized unless reviewed by this office for compliance with Code.  Modifications to reviewed plans must be submitted to this office by the Architect/Civil Engineer for review prior to final inspection.  If an Architect or Civil Engineer is not required by RS 37:155, revisions shall be submitted by the Owner.  Submittals shall include plans, completed application, a minimum $55.00 review fee, and a copy of the most current plan review letter.

Compliance with code requirements for fire protection systems, such as Fire Alarm, Sprinkler and Suppression Systems, is determined by separate shop drawing submittal and is not included in this review.

This review applies to work indicated in the drawings or specifications.  Existing portions of the facility of building unaffected by the new work shall comply with LAC 55:103B thru 55:103F.

This review shall in no way permit and/or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

This review is valid for 180 days from the date of this letter.  Construction permits must be issued and/or construction must commence within this time period.

This office requires certification of the completed project in accordance with the approved documents (certificate enclosed).

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below two (2) to three (3) weeks in advance.  The plans stamped reviewed by this office must be available on job site at time of inspection.  Certificate of completion must be provided to the inspecting Deputy for final inspection.

REVIEWED BY:
JOHN LAUDUN
ARCHITECT

CC:
Quiznos
Jefferson Parish Fire Prevention
Sam Vanover*
New Orleans District*     5045685500