Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

April 17, 2006

Mr. Bhatta Charya

Department of Safety & Permits

1300 Perdido St Suite 7E06

New Orleans, LA 70112

RE:  
Job No: 06COM00054


Location 2801 Magazine St.


Interior Renovation – Quiznos #9880

Dear Mr. Charya,

The following are responses to the letter dated Feb 2, 2006, from New Orleans Plan Review:

1. Mechanical Note #2 contradicts with the Mechanical Plan.  Line Size for Rooftop A/C unit #1 needs to be checked as main duct flow rate appears to be higher than 1000CFM.  State duct size for primary and secondary ducts for clarity.  

Answer.  Please see attached for Rooftop A/C unit information.  Note #2 was inadvertently miss typed as CFM instead of FPM.   Note #2 should read:  

CONCEALED DUCTWORK TO BE UL-181, CLASS I, FIBERGLASS DUCTBOARD.  DUCTS SHALL BE SIZED TO LIMIT MAIN DUCTS TO 1,000 FPM AND SECONDARY DUCTS TO 600 FPM.  TO BE INSTALLED PER SMACNA STANDARDS.

2. Show structural support for 50-gallon hot water heater.  

Answer.  Additional information has been provided to show structural support for 50-gallon hot water heater, please see attached.

Sincerely,

David Dammon

Project Manager

cc:  LAWRENCE J SCHOFIELD

