SECTION 15290

DUCTWORK INSULATION
1 PART 1 GENERAL

 .1 
SECTION INCLUDES

A. Ductwork insulation.

B. Duct Liner.

C. Insulation jackets.

   .2 
PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION

    
Not Used

 .3 
RELATED SECTIONS

A. Section 15190 – Mechanical Identification

B. Section 15890 – Ductwork: Glass fiber ductwork

C. Section 15890 – Ductwork: Duct liner.

 .4 
REFERENCES

A. ASTM B209 – Aluminum and Aluminum Alloy Sheet and Plate.

B.  ASTM C518 – Steady-State Heat Flux Measurements and Thermal 
Transmission Properties by means of the heat flow meter apparatus.

C. ASTM  C553 – Mineral Fiber blanket and felt 

   insulation.

D. ASTM  C612 – Mineral Fiber block and board thermal   

   insulation.

E. ASTM E84 – Surface burning characteristics of      

   building materials.

F. ASTM E96 – Water vapor transmission of materials.

G. NFPA 255 – Surface burning characteristics of  

   building materials.

H. SMACNA – HVAC Duct construction standards – metal  

   and flexible.

I. UL 723 – Surface burning characteristics of building  

   materials.

.5 
SUBMITTALS

A. Submit under provisions of Section 01300.

B. Product data:  Provide product description, list of materials and thickness for each service, and locations.

C. Samples: Submit two samples of any representative size illustrating each Insulation type.

D. Manufacturer’s installation instructions: Indicate  

procedures which ensure acceptable workmanship and

installation standards will be achieved.

.6
QUALITY ASSURANCE

A. Materials: Flame spread/smoke developed rating of 25/50 in accordance with NFPA 255.

.7 
QUALIFICATIONS

A. Applicator:  Company specializing in performing the work of this section with Minimum three years experience.

.8 
DELIVERY, STORAGE AND HANDLING

    
Not Used

.9 
ENVIRONMENTAL REQUIREMENTS

A. Maintain ambient temperatures and conditions required by manufacturers of Adhesives, mastics, and insulation cements.

B. Maintain temperature during and after installation for minimum period of 24 Hours. 

2 PART 2 PRODUCTS

       .1 
GLASS FIBER, FLEXIBLE

A. Manufacturers:

Not Used

B. Insulation:  ASTM C553 flexible, noncombustible blanket.

1. ‘K’ value: ASTM C518, 0.29 at 75 degrees F.

2. Maximum service temperature: 250 degrees F.

3. Maximum moisture absorption: 0.50 percent by volume.

4. Density: 1.0 lb/cu ft.

C. Vapor Barrier Jacket

1. Kraft  paper reinforced with glass fiber yarn and bonded to aluminized

Film 0.0032 inch vinyl.

2. Moisture vapor transmission:  ASTM E96; 0.04 perm.

3. Secure with pressure sensitive tape.

D. Vapor  Barrier Tape

1. Manufacturers:

Not Used

2. Kraft paper reinforced with glass fiber yarn and bonded to aluminized film, with pressure sensitive rubber based adhesive. 

E. Tie Wire

1. Annealed steel, 16 gages (1.5 mm).

.2
GLASS FIBER, RIGID

A. Manufacturers:

Owens Corning Orequal

B. Insulation:  ASTM C612; rigid, noncombustible blanket.

1. Maximum service temperature: 250 degrees F.

2. Maximum moisture absorption: 0.20 0.50 percent by volume.

3. Density:  1.0 lb/cu ft/

C. Vapor Barrier Jacket

1. Kraft paper reinforced with glass fiber yarn and bonded to aluminized film 0.0032 inch vinyl.

2. Moisture vapor transmission: ASTM E96; 0.04 1.3 perm.

3. Secure with pressure sensitive tape.

D. Vapor Barrier Tape

1. Manufacturers:

Not Used

2. Kraft paper reinforced with glass fiber yarn and bonded to aluminized film, with pressure sensitive rubber based adhesive.

.3
JACKETS

A. Canvas Jacket:  UL listed

1. Fabric:  6 oz/sq. yd 220 g/sq. m, plain weave cotton treated with dilute fire retardant lagging adhesive.

B. Outdoor Jacket: Asphalt impregnated and coated mineral fiber sheet, 36 lb/sq.

    C. Aluminum Jacket:  ASTM B209

1. Thickness:  0.020 sheet.

2. Finish:  Embossed.

3. Joining:  Longitudinal slip joints and 2 inch laps.

4. Fittings:  0.016 inch thick die shaped fitting covers with factory attached

Protective liner.

5. Metal Jacket Bands:  3/8 inch 0.015 thick aluminum.

.4
GLASS FIBER DUCT LINER, FLEXIBLE

A. Manufacturers:

Owens Coring Orequal

B. Insulation:  ASTM C553; flexible, noncombustible blanket.

1. ‘K’ value:  ASTM C518, at 75 degrees F 

2. Maximum service temperature: 250 degrees F.

3. Density: 2.0 lb/cu ft.

4. Maximum velocity on Coated Air side: 4,000 ft/min.

C. Adhesive

1. Manufacturers:

Not Used

2. Waterproof fire-retardant type.

D. Liner Fasteners: Galvanized steel, self-adhesive pad, welded with integral head.

3 PART 3 EXECUTIVE

.1 
EXAMINATION

A. Verify that ductwork has been tested before applying insulation materials.

B. Verify that surfaces are clean, foreign material removed, and dry.

.2
INSTALLATION

A. Install materials in accordance with manufacturer’s instructions.

B. Insulated ductwork conveying air below ambient 

   temperature:

1. Provide insulation with vapor barrier jackets.

2. Finish with tape and vapor barrier jacket.

3. Continue insulation through walls, sleeves, hangers, and other duct penetrations.

4. Insulate entire system including fittings, joints, flanges, fire dampers, flexible connections, and expansion joints.

C.  Insulated ductwork conveying air above ambient 

    temperature:

1. Provide with or without standard vapor barrier jacket.

2. Insulate fittings and joints.  Where service access is required, bevel and seal ends of insulation.

D. For ductwork exposed in mechanical equipment rooms or in finished spaces below 10 feet 3 meters above finished floor, finish with canvas jacket sized for finish painting aluminum jacket.

E. For exterior applications, provide insulation with vapor barrier jacket.  Cover with outdoor jacket with caulked aluminum jacket with seams located on bottom side of horizontal duct section. 

F. External Duct Insulation Application;

1. Secure insulation with vapor barrier with wires and seal jacket joints with vapor barrier or tape to match jacket.

2. Secure insulation without vapor barrier with staples, tape, or wires.

3. Install without sag on undersides of ductwork.  Use adhesive or mechanical fasteners where necessary to prevent sagging.  Lift ductwork off trapeze hangers and insert spacers.

4. Seal vapor barrier penetrations by mechanical fasteners with vapor barrier adhesive.

5. Stop and point insulation around access doors and damper operations to allow operations without disturbing wrapping.

G. Duct and Plenum liner application:

1. Adhesive insulation with adhesive for 90 100 percent coverage.

2. Secure insulation with mechanical liner fasteners.  Refer to SMACNA Standards for spacing.

3. Seal liner smooth joints.

4. Seal liner surface penetrations with adhesive.

5. Duct dimensions indicated are net inside dimensions required for airflow.  Increase duct size to allow for insulation thickness.

   .3
TOLERANCE

A. Substituted insulation materials shall provide thermal resistance within 10 Percent at normal conditions, as materials indicated.



END OF SECTION
PAGE  
Section 15290 Page 1 of 4

