July 16, 2002

Mr. Kenneth Robichaux

Office of State Fire Marshal

Code Enforcement and Building Safety.

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE:
P0241819

Dear Mr. Robichaux,

I have reviewed the drawings and made the changes that are noted in your letter dated July 2,2002.

1. The details of the tanks are shown on DWG. A-5.

2. The location of the tanks is shown on DWG. C-1.

3. The tanks are double walled and have their own dike.

4. The tanks are less than 12,000 gallons and are double walled with the proper overfill alarm.

5. The tanks are less than 12,000 gallons and are double walled with the proper overfill alarm.

6. The Fuel tank and Diesel tank are vented with the proper equipment.

7. Sheet M-1 has been revised to show the proper NFPA 90A:4-4.2(1)

8. This site does require Single Phase and the panels where changed to reflect it. The panel from the pump house are on ckt. #19 and the panel from the fuel shed are on ckt. #22. The panels are 120/240V, single phase.

9. The generator is future. A grounding design will be completed at that time.

Please call me with any questions that you may have.

Thank you,

Chuck Dammon

Vice President/Project Manager

