August 1, 2000

Ashok Kukreja

Plan Review Architect

Office of State Fire Marshall

5150 Florida Ave

Baton Rouge, LA  70806

Re;
PO156596 Standard Materials office


Renovations

Dear Sir;

  The above work has all been completed and inspected by the local Fire district.  Only one item remains to be addressed, and this involves the existing facility.

  As shown on the enclosed plan, the existing hallway leading to this emergency exit is only 33-inches wide.  When the contractor installed the new 36-inch wide door, it wouldn’t fully open and allow easy passage, because it tried to open into the 33-inch wide hallway.  He then installed a 32-inch wide door, allowing easy passage.

  This exit is a second means of egress from the office area, the other being an interior stair.  This exit has proven to be an easily traveled route for the employees, and seems to work well with the 33-inch wide corridor.  There are approximately 10 employees on the 2nd floor.

  Please allow an exception to the code for the door width (32 inches) and the existing hall width (33- inches).  Although no other accommodations are made for wheel chairs on this floor, wheelchairs will pass through the opening and make the turn into the hallway.

  Should you need further information regarding this item, please call me at 504-649-5832

Sincerely,

Emmett G (Pete) Dammon P.E.,

Attachments

1. Drawing A-2 Showing area of appeal

2. Photos of hallway and door exit.

3. Copy of Fire Marshall letter

EGD/plc

