November 2, 2000

TO:
 Felicia Cooper, Architect


Office of State Fire Marshall


5150 Florida Ave


Baton Rouge, LA  70806

RE;
Jay Martin Marine PO211693

Appeal to requirement to limit size of


Fire Door to 120 S.F.

Dear Ms. Cooper;


As can be seen on the attached drawing, the fire door in question separates the shop area of the Marine service from the sales area.  In order to bring new boats into the sales display area, the owner will bring the boat and trailer combination through the shop.  The door will only be used during this period of time, then closed until boats are changed out, etc.. Following initial start up, this activity will be on an infrequent and short duration basis, again.


The problem lies in the fact that many of the boats that need to be displayed will be of a height (trailer plus boat), that requires more than the twelve feet of height, dictated when using a ten foot wide door.


The Door Company has no problem in building the fire door the size of 12 ft wide and 14 ft high.  We ask that the infrequency of use be considered as an approved equivalency  to the 120 sq. ft requirement.

Sincerely,

Emmett G (Pete) Dammon P.E.,

Attachment


Fire door spec sheet.


Check


Copy of dwg A-1

EGD/plc

