March 13, 2000

Otis V. Ramke Jr.  Architect

Office of State Fire Marshall

5150 Florida Ave

Baton Rouge, LA  70809

RE;
PO174000, Historical Fritchie-Salmen House

Dear Mr. Ramke;

Mike Faulk informed us that you had met with and told him the following requirements to adhere to.

1.
Front doors remain as is and delete exit sign on drawing.

2.
Add exit signs to second dining room on left with exit signs leading out to side foyer and egress door.

3.    Reverse side foyer egress doors to swing out. 

4.    Extend side foyer exit platform and stairs to meet code.

5.
Remove rear doors leading to hall and install exit signs 

     leading out to rear.

6.
Doorman will be on duty on every function with a clicker. 


Keeping count of heads entering and leaving.

7. Install handicap ramp on the west side of building. Per 

code. 

I would appreciate your favorable response to these items.







Sincerely,







Emmett G (Pete) Dammon P.E.,

Attachments

1. Copy of previous letter

2. Drawing of proposed items

plc/EGD

