April 26, 2000

Mr. Don P. Zeringue, Architect

Office of Louisiana Fire-Marshall

5150 Florida Ave.

Baton Rouge, LA  70846

RE;
P0 203598 (NOCHC)

Dear Sir;

1.   Reference is made to items listed in your review letter for the project.

2. 101: 5-1.3.2.1

The area described in your letter as an exit enclosure is not an enclosure as such.  The area in the basement of an early 1800 style building, and there are no doors other than the one exit door leading outside, therefore, we ask that pipe be allowed to cross the hallway at this location.

a) LRS 40: 1731

b) 4.9.4(2) your review of the drawing shows that we failed to add an extension to the handrail of the ramp.  We are extending that rail. The steps do presently show an extension to the steps.

c) & c) agreed, the drawings presently reflect this.

3. 101: 5-1.5 Agreed.  The corridors have 12 ft + ceilings on all 
upper levels.  The basement has low headroom ceilings.  We are not running duct in walking areas of the basement.

4. Agreed.

5. Agreed.

6. There is no fire alarm system in the building presently.  It is our understanding that another consultant is designing a fire detection and alarm system for the building.






Sincerely,







Emmett G (Pete) Dammon P.E.,

EGD/plc
1

