January 10, 2000

TO:
Don P. Zeringue


Architect Supervisor








State Fire Marshall Office




 

5150 Florida Blvd.

Baton Rouge, LA  70806

RE;
P0175731

Camellia Gardens Apartments


Possum Hollow Rd Slidell, LA


Fire Marshall Drawing Changes

The following changes were made to drawings, per your review.  Please refer to your comments.
DWG -A-1

1.   Revised note 2D to be 38” minimum from floor.

2.   Revised parking lot configuration added HCP parking.

DWG -A-2

1.   Moved front door back 48”

2.   Added note to provide storage for flammable products in arts & 

  crafts.

3.   Provided stairs to stage in Activity room.

4.   Added vent in Beauty Salon.

5.   Provided HCP toilets in Chapel area.

6.   Moved stairwell door.

7.   Added fire doors to first & second floor.

8.   Fire rated all walls.

9.   Added note for receptionist.

10.   Added note to provide HCP elevator from MFG.

DWG-A-3

1. Rearranged laundry room to be HCP assemble with HCP 

appliances.

2.  Revised drawings to show HCP seat on all HCP units.

DWG-A-7

1. Added notes to provide 1 hr firewalls & all appliance to be HCP.

DWG-A-8 

1. Added notes showing firewalls and U.L. ratings.

DWG-A-9

1. Revised drawings to show HCP bathroom & requirements.

DWG-A-10 

1. Revised drawings to show HCP bathroom & requirements.

DWG-A-11

1.  Added ADA requirements for laundry room.

DWG-A-12

1.  Relocated stairwell doors.

2.  Added fire doors & U.L. ratings

3.  Added 2 HCP spaces.

4.  Added firewalls on chimney and U.L. rating.

DWG-A-13

1.   Added HCP appliances and firewall.

DWG-A-16

1.  Revised all cathedral ceilings to be U.L. rated.

DWG-A-17

1.  Revised building sections to show U.L. ratings.

DWG-A-18

1.  Revised building sections to show U.L. ratings.

DWG-A-21


     1.
      Revised drawing to show height of stairs.

PAGE  
1

