August 28, 2001

Ms. Cynthia Obier/Architect

Office of State Fire Marshal

5150 Florida Boulevard

Baton Rouge, Louisiana   70806

RE:
PO226724/St. Tammany Association for Retarded Citizens

Dear Ms. Obier,

In order that we preserve the classroom layout of our first submission, the owners have elected to provide a sprinkler system throughout the facility, including the drive up cover at the entrance.

In doing so, the following changes will be made to the project.  The rating is changed to Type VI, unprotected, sprinkled:

1. Attic separation (smoke walls) will be deleted.

2. Corridor one hour separation will be deleted.

3. Rated doors in the corridors will be changed to non-rated.

4. Contractor will have option to frame with wood or metal.

We are sending you revised drawings for your approval.

Sincerely,

Emmett G. (Pete) Dammon, P.E.

Louisiana License #8796

EGD:clh

