Textron
Questions:

1. Existing slab – new bldg.? Demolish old.

2. Duct on one side – blow _____________ or duct each side.

3. (2) exhaust fans – why?  Modulating? Or damper control

4. Variable volume or constant volume w/modulation of refrigeration or on-off.

5. Wall, roof panel seals


Wall to roof joint seals


Door seal


Vehicle roll up door panel seals


Walk in door seals


Door closers – quick close

6. R22?

7. 10 KW vehicle _________ - how many? At one time 2 __________ lines

8. 0.10” s.p. w.p. load on brush away panels can they stand pressure?  Door load? @ .036 psi

9. O/A 5000 min.

10. capture ____ for hood exhaust = 2(6) = 12 ____ (500fpm) = 6,000 cfm? Is this same cfm @ #9.

11. Is control system part of unitary AHU?

12. Dampers may be duct ________________

13. Single room thermostat?

14. Two exhaust systems sect. 15010 – par 1.5?  Same as hood exhaust?

15. ACGIH industrial ventilation handbook.

16. ? Step control (4) for cooling?  How?  Screw type compressor

17. Are questions relative to HVAC design?

18. Use reheat for humidification.

19. Will a control company be employed?

20. Temperature and humidity programmable controller to control temp and humidity?  Is this part of unitary?

21. Control system responsibility _____________ control company required.

22. What is the lighting requirement ___________?

23. What heat producing equipment _______________
24. How many persons employed in space?

25. Four way refrigerant reversing valve?

26. Need sec. 15810 duct work and duct work ________

27. Any leak proof construction – walls, doors

28. How do we determine leakage on wall panels

29. How do we determine leakage in _______ door panels

30. Leakage on wall to roof?  Bottom of wall panels?

31. Do we need pressure relief wall dampers?  Press controller

