January 31, 2005

Mr. Anthony Emukah

City of New Orleans

Plan Review Division

1300 Perdido Street, Ste 7E06

New Orleans, LA  70112

RE:
Permit NO – 04COM-01256


19401 Chef Menteur, Bldg. 19


New Construction

Dear Mr. Emukah,

With regards to our conversation today and your letter dated Jan 31, 2005, please accept the following answers to your questions.

ARCHITECTURAL

1. Please indicate the Construction Type of this building and verify that the building area complies with Table 503 IBS.

Answer:

a.  The construction type is IIB, non-combustible, (See cover sheet of drawings).

b. The building occupancy is Type B, Table 503 shows an allowable area of 23,000 s.f. for a group B building.  This building has a total of 21, 234 s.f., and meets the requirements of Table 503.

2. This information was previously submitted.

3. Please verify that the Paint Booth will comply with NFPA 33 with particular reference to Chapter 3:  Construction of and Design of Spray Area, Spray Rooms, and Spray Booths; Chapter 5: Ventilation; Chapter 7: Protection.

Answer:

The paint booth is being constructed to comply with NFPA 33, with particular reference to Chapter 3: Construction and Design, Chapter 5: Ventilation, and Chapter 7:, Protection.

4. Approval from the State Fire Marshal is required.
Answer:

Per Ms. Long, proof is not required, as we have submitted this.

ELECTRICAL

1. All wiring in Paint area shall comply with NEC-2002 article 516 [Plan E-1].

Answer:

The following shall apply:  all wiring in paint areas (booths) will comply with NEC-2002, Article 5161.

MECHANICAL

The following shall apply:

1. All galvanized sheet metal duct work shall be constructed as per proper gauges to meet the requirements of SMACCNA manual, ASHRAE guide edition 1997 and as delineated by NFPA Standard 90-A.  Please note that all commercial installation shall meet minimum standards and that all areas used as “part of the HVAC System” shall be devoid of combustible materials.

2. Galvanized round ducts shall be of gauges that meet commercial standard.  Flex ducts shall be UL Class I – approved and shall not exceed 14’ – 0” in. length for commercial installation when tied to the main supply ducts.

3. Air distribution systems shall be equipped with smoke detectors listed and labeled for installation in air distribution systems, as required by Section 606.1 IMC.

4. Smoke detectors shall be installed in return air systems with design capacity greater than 2,000 cfm, in return air duct or plenum upstream of any filters, exhaust air connections, outdoor air connections, or decontamination equipment and appliances as per Section 606.2.1 IMC.

Sincerely,
Emmett G. (Pete) Dammon, P.E.
