
SECTION 15190PRIVATE 


MECHANICAL IDENTIFICATION
PART 1
GENERAL
.1

SECTION INCLUDES


A.
Nameplates.


B.
Tags.


C.
Stencils.


D.
Pipe Markers.

.2seq level2 \h \r0 

RELATED SECTIONS

A.
Section 09900 ‑ Painting:  Identification painting.

.3seq level2 \h \r0 

REFERENCES

A.
ASME A13.1 ‑ Scheme for the Identification of Piping Systems.

.4seq level2 \h \r0 

SUBMITTALS

A.
Submit under provisions of General Conditions.


B.
Submit list of wording, symbols, letter size, and color coding for mechanical identification.


C.
Submit valve chart and schedule, including valve tag number, location, function, and valve manufacturer's name and model number.


D.
Product Data:  Provide manufacturers catalog literature for each product required.


E.
Samples:  Submit two tags  2 x 6 inch in size.


F.
Manufacturer's Installation Instructions:  Indicate special procedures, and installation.

.5seq level2 \h \r0 

PROJECT RECORD DOCUMENTS

A.
Submit under provisions of Section 01700.


B.
Record actual locations of tagged valves.

PART 2

seq level1 \h \r0 

seq level2 \h \r0 
PRODUCTS

.1

NAMEPLATES

A. 

.2

seq level2 \h \r0 

TAGS

A.  seq level3 \h \r0 

seq level4 \h \r0 Plastic Tags: Laminated three‑layer plastic with engraved   black letters on light contrasting background color.  Tag size minimum 1‑1/2 inch (40 mm) diameter square.


seq level0 \h \r2 

seq level1 \h \r2 

seq level2 \h \r1 

seq level3 \h \r0 

seq level4 \h \r0 

seq level5 \h \r0 

seq level6 \h \r0 

seq level7 \h \r0 
.3

seq level2 \h \r0 

STENCILS



Not Used

.4
seq level2 \h \r0 
PIPE MARKERS

A.  
seq level3 \h \r0 

seq level4 \h \r0 
Color: Conform to ASME A13.1.


B.  
Plastic Pipe Markers: Factory fabricated, flexible, semi‑   rigid plastic, preformed to fit around pipe or pipe covering; minimum information indicating flow direction arrow and identification of fluid being conveyed.


C. 
Plastic Tape Pipe Markers: Flexible, vinyl film tape with pressure sensitive adhesive backing and printed markings.


D. 
Underground Plastic Pipe Markers: Bright colored continuously 
       printed plastic ribbon tape, minimum 6 inches (150 mm) wide              by 4 mil (0.10 mm) thick, manufactured for direct burial                
service.

.5

seq level2 \h \r0 

CEILING TACKS



Not Used

PART 3

seq level1 \h \r0 

seq level2 \h \r0 

seq level3 \h \r0 
EXECUTION

.1

PREPARATION

A. 
Degrease and clean surfaces to receive adhesive for identification materials.


B. 
Prepare surfaces in accordance with Section 09900 for stencil painting.    
.2

seq level2 \h \r0 

INSTALLATION

A.
Install plastic nameplates with corrosive‑resistant mechanical fasteners, or adhesive.  Apply with sufficient adhesive to ensure permanent adhesion and seal with clear lacquer.


B.
Install tags with corrosion resistant chain.

C.
Apply stencil painting in accordance with Section 09900.


D.
Install plastic pipe markers in accordance with manufacturer's instructions.


E.
Install plastic tape pipe markers complete around pipe in accordance with manufacturer's instructions.


F.
Install underground plastic pipe markers 6 to 8 inches (150 to 200 mm) below finished grade, directly above buried pipe.


G.
Identify air handling units, pumps, heat transfer equipment, tanks, and water treatment devices with plastic nameplates.  Small devices, such as in‑line pumps, may be identified with tags.


H.
Identify control panels and major control components outside panels with plastic nameplates.


I.
Identify thermostats relating to terminal boxes or valves with nameplates.


J.
Identify valves in main and branch piping with tags.


K.
Identify air terminal units and radiator valves with numbered tags.


L
.
Tag automatic controls, instruments, and relays. Key to control schematic.


M.
Identify piping, concealed or exposed, with plastic tape pipe markers. Use tags on piping 3/4 inch (20 mm) diameter and smaller. Identify service, flow direction, and pressure.  Install in clear view and align with axis of piping.  Locate identification not to exceed 20 feet (6 m) on straight runs including risers and drops, adjacent to each valve and Tee, at each side of penetration of structure or enclosure, and at each obstruction.


N.
Identify ductwork with plastic nameplates. Identify with air handling unit identification number and area served.  Locate identification at air handling unit, at each side of penetration of structure or enclosure, and at each obstruction.


O.
Provide ceiling tacks to locate valves or dampers above T‑bar type panel ceilings.  Locate in corner of panel closest to equipment.

.3

seq level2 \h \r0 

SCHEDULES


Equipment
Identification

Background  Lettering



Type






Size Color
SizeColor


END OF SECTION
PAGE  
1

