
SECTION 15410PRIVATE 


PLUMBING PIPING

Provisions of the contract including General and Supplementary General Conditions and the General Requirements apply to the work of this section.
1 PART 1 GENERAL


.1

SECTION INCLUDES



A.
Pipe and pipe fittings.



B.
Valves.



C.
Sanitary sewer piping system.



D.
Domestic water piping system.



E.
Storm water piping system.


.2
seq level2 \h \r0 
PRODUCTS FURNISHED BUT NOT INSTALLED UNDER THIS SECTION



A.
Section 03300- Cast-in place concrete and 04300 – Unit masonry: Placement of pipe sleeves.


.3

seq level2 \h \r0 

RELATED SECTIONS



A.
Section 02222 ‑ Excavating.



B.
Section 02223 ‑ Backfilling.



C.
Section 02225 ‑ Trenching.



D.  
Section 09900 ‑ Painting.





E.
Section 15260 ‑ Piping Insulation.



F.
Section 15430 ‑ Plumbing Specialties.

G. Section 15440 ‑ Plumbing Fixtures.



H.
Reference to General Conditions.


.4
seq level2 \h \r0 
REFERENCES



A.
ANSI B31.9 ‑ Building Service Piping.



B.  ASME B16.3 ‑ Malleable Iron Threaded Fittings.



C.
ASME B16.4 ‑ Cast Iron Threaded Fittings Class 125 and 250.



D.
ASME B16.18 ‑ Cast Bronze Solder‑Joint Pressure Fittings.



E.
ASME B16.22 ‑ Wrought Copper and Bronze Solder‑Joint Pressure Fittings



F.
ASTM A74 ‑ Cast Iron Soil Pipe and Fittings.



G.
ASME B16.32 ‑ Cast Copper Alloy Solder‑Joint Fittings for Sovent Drainage Systems.



H.
ASTM B88 ‑ Seamless Copper Water Tube.



I.
ASTM C564 ‑ Rubber Gaskets for Cast Iron Soil Pipe and Fittings.



J.
ASTM D1785 ‑ Poly (Vinyl Chloride) (PVC) Plastic Pipe,        Schedules 40, 80, and 120.



K.
ASTM D2241 ‑ Poly (Vinyl Chloride) (PVC) Plastic Pipe (SDR‑PR).



L.
ASTM D2466 ‑ Poly (Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40.



M.
ASTM D2564 ‑ Solvent Cements for Poly (Vinyl Chloride) (PVC) Plastic Pipe and Fittings.



N.
ASTM D2729 ‑ Poly (Vinyl Chloride) (PVC) Sewer Pipe and Fittings.



O.
ASTM D2855 ‑ Making Solvent‑Cemented Joints with Poly (Vinyl Chloride) (PVC) Pipe and Fittings.



P.
CISPI 301 ‑ Cast Iron Soil Pipe and Fittings for Hubless Cast Iron Sanitary Systems.



Q.
CISPI 310 ‑ Joints for Hubless Cast Iron Sanitary Systems.






.5
seq level2 \h \r0 
SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data: Provide data on pipe materials, pipefittings, valves, and accessories.  Provide manufacturers catalog information.  Indicate valve data and ratings.


.6
seq level2 \h \r0 
PROJECT RECORD DOCUMENTS



A.
Submit under provisions of Section 01700.



B.
Record actual locations of lines, valves, unions, etc.


.7

seq level2 \h \r0 

OPERATION AND MAINTENANCE DATA



A.
Submit under provisions of Section 01700.



B.
Maintenance Data:  Include installation instructions, spare parts lists, exploded assembly views.


.8

seq level2 \h \r0 

QUALITY ASSURANCE



A.
Valves: Manufacturer's name and pressure rating marked on valve body.



B.
Welding Materials and Procedures: Conform to ASME Code.



C.
Welders Certification: In accordance with ASME Sec 9 



seq level2 \h \r0 

.9
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Perform Work in accordance with State of Louisiana plumbing code.



B.
Conform to applicable code for installation of backflow prevention devices.



C.
Provide certificate of compliance from authority having jurisdiction indicating approval of installation of backflow prevention devices.


.10seq level2 \h \r0 
DELIVERY, STORAGE, AND HANDLING



A.
Deliver, store, protect and handle products to site under provisions of Section 01600.



B.
Accept valves on site in shipping containers with labelling in place.  Inspect for damage.



C.
Provide temporary protective coating on cast iron and  steel valves.



D.
Provide temporary end caps and closures on piping and fittings.  Maintain in place until installation.



E.
Protect piping systems from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.


.11seq level2 \h \r0 
ENVIRONMENTAL REQUIREMENTS



A.
Do not install underground piping when bedding are wet or frozen.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2 PRODUCTS


.1

SANITARY SEWER PIPING, BURIED BEYOND 5 FEET (1500 mm) OF BUILDING



A.seq level3 \h \r0 
PVC Pipe: ASTM D3033 or D3034, SDR 35.




1.
Fittings: PVC.




2.
Joints: ASTM F477, elastomeric gaskets.


.2
seq level2 \h \r0 

seq level3 \h \r0 
SANITARY SEWER PIPING, BURIED WITHIN 5 FEET (1500 mm) OF BUILDING



A.
Cast Iron Pipe: ASTM A74 service weight.




1.
Fittings: Cast iron.




2.
Joints: Hub‑and‑spigot, CISPI HSN compression type with ASTM C564 neoprene gaskets or lead and oakum.


.3
seq level2 \h \r0 

seq level3 \h \r0 
SANITARY SEWER PIPING, ABOVE GRADE



A.
Cast Iron Pipe: ASTM A74, service weight.




1.
Fittings: Cast iron.


.4
seq level2 \h \r0 

seq level3 \h \r0 
WATER PIPING, BURIED BEYOND 5 FEET (1500 mm) OF BUILDING



A.seq level3 \h \r0 
PVC Pipe: ASTM D1785, Class 150 C-900.




1.
Fittings:  ASTM D2466, PVC.




2.
Joints: ASTM D2855, solvent weld with ASTM D2564 Solvent cement.


.5
seq level2 \h \r0 

seq level3 \h \r0 
WATER PIPING, BURIED WITHIN 5 FEET (1500 mm) OF BUILDING



A.
Copper Tubing: ASTM B88, Type L, hard drawn. 




1.
Fittings: ASME B16.18, cast bronze or ASTM B16.22 wrought copper and bronze.




2.
Joints: ASTM B32, solder, Grade 95TA.


.6

seq level2 \h \r0 

seq level3 \h \r0 

WATER PIPING, ABOVE GRADE



A.
Copper Tubing: ASTM B88, Type L, hard drawn.




1.
Fittings: ASME B16.18, cast bronze, or ASME B16.22 wrought copper and bronze.




2.
Joints: ASTM B32, solder, Grade 95TA.


.7
seq level2 \h \r0 

seq level3 \h \r0 
VALVES




Furnish and install all valves, unions, stops, connections, etc. shown on plans and necessary to make a complete system in working order.  Provide valves on inlet and outlet of all equipment and fixtures and on branch lines to fixtures or group of fixtures.




Valves and unions shall be as follows:




Copper Pipe

2” and Less

Over 2”



Gate Valve

Crane 1320

Crane 461




Globe Valve

Crane 1310

Crane 359




Unions


Crane  633
   
Crane Std. Gal




Check Value

Crane 1303

Crane 373




Iron Pipe

2” and Less

Over 2”




Gate Valve

Crane  440

Crane 461




Globs Valve

Crane    7

Crane 359




Unions


Crane  663






Check Valve

Crane 1303

Crane 373

Valves as manufactured by Dezurich, Wadsworth, or equivalent will be accepted.

3

seq level1 \h \r0 

seq level2 \h \r0  PART 3 EXECUTION


.1

EXAMINATION



A.
Verify excavations under provisions of Section 01039. 



B.
Verify that excavations are to required grade, dry, and not over‑excavated.


.2

seq level2 \h \r0 

PREPARATION



A.
Ream pipe and tube ends.
Remove burrs.  



B.
Remove scale and dirt, on inside and outside, before assembly.



C.
Prepare piping connections to equipment with flanges or unions.


.3
seq level2 \h \r0 
INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Provide non‑conducting dielectric connections wherever jointing dissimilar metals.



C.
Route piping in orderly manner and maintain gradient.



D.
Install piping to conserve building space and not interfere with use of space.



E.
Group piping whenever practical at common elevations.



F.
Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.



G.
Provide clearance for installation of insulation and access to valves and fittings.



H.
Provide access where valves and fittings are not exposed. Coordinate size and location of access doors.



I.
Establish elevations of buried piping outside the building to ensure not less than 2 ft of cover.



J.
Where pipe support members are welded to structural building framing, scrape, brush clean, and apply one coat of zinc rich primer to welding.



K.
Provide support for utility meters in accordance with requirements of utility companies.



L.
Prepare pipe, fittings, supports, and accessories not prefinished, ready for finish painting.  Refer to Section 09900.



M.
Excavate in accordance with Sections 02222 and 02225 and for work of this Section.



N.
Backfill in accordance with Sections 02223 and 02225 for work of this Section.



O.
Install bell and spigot pipe with bell end upstream.



P.
Install valves with stems upright or horizontal, not inverted.

.4

seq level2 \h \r0 

APPLICATION



A.
Use grooved mechanical couplings and fasteners only in accessible locations.



B.
Install unions downstream of valves and at equipment or apparatus connections.



C.
Install brass male adapters each side of valves in copper piped system.  Sweat solder adapters to pipe.



D.
Install ball valves for shut‑off and to isolate equipment, part of systems, or vertical risers.



E.
Install pipe markers on both sides of valves located above ceiling to indicate direction of flow.


.5
seq level2 \h \r0 
ERECTION TOLERANCES



A.
Establish invert elevations, slopes for drainage to 1/8 inch per foot minimum.  Maintain gradients.



B.
Slope water piping and arrange to drain at low points.


.6

seq level2 \h \r0 

DISINFECTION OF DOMESTIC WATER PIPING SYSTEM



A.
Prior to starting work, verify system is complete, flushed and clean.



B.
Ensure PH of water to be treated is between 7.4 and 7.6 by adding alkali (caustic soda or soda ash) or acid (hydrochloric).



C.
Inject disinfectant, free chlorine in liquid, powder, tablet or gas form, throughout system to obtain 50 to 80 mg/L residual.



D.
Bleed water from outlets to ensure distribution and test for disinfectant residual at minimum 15 percent of outlets.



E.
Maintain disinfectant in system for 24 hours.



F.
If final disinfectant residual tests less than 25 mg/L, repeat treatment.



G.
Flush disinfectant from system until residual equal to that of incoming water or 1.0 mg/L.



H.
Take samples no sooner than 24 hours after flushing, from 10 percent of outlets and from water entry, and analyze in accordance with AWWA C651.
PAGE  
1

