
SECTION 16195PRIVATE 


ELECTRICAL IDENTIFICATION
1 PART 1 
GENERAL


.1

SECTION INCLUDES



A.
Nameplates and labels.



B.
Wire and cable markers.



C.
Conduit markers.


.2

seq level2 \h \r0 

RELATED SECTIONS



A.
Section 09900 ‑ Painting.


.3

seq level2 \h \r0 

REFERENCES



A.  
ANSI/NFPA 70 ‑ National Electrical Code.


.4

seq level2 \h \r0 

SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data:  Provide catalog data for nameplates, labels, and markers.



C.
Manufacturer's Instructions:
 Indicate application conditions and limitations of use stipulated by Product testing agency specified under regulatory requirements.  Include instructions for storage, handling, protection, examination, preparation and installation of Product.


.5

seq level2 \h \r0 

REGULATORY REQUIREMENTS



A.
Conform to requirements of ANSI/NFPA 70.



B.
Furnish products listed and classified by Underwriters Laboratories, Inc.  as suitable for purpose specified and shown.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2 
PRODUCTS


.1

NAMEPLATES AND LABELS



A.
Nameplates:  Engraved three‑layer laminated plastic, black letters on white  background.



B.
Locations:




1.
Each electrical distribution and control equipment enclosure.




2.
Communication cabinets.



C.seq level3 \h \r0 
Letter Size:




1.
Use 1/8  inch  letters for identifying individual equipment and loads.




2.
Use 1/4 inch letters for identifying grouped equipment and loads.



D.seq level3 \h \r0 
Labels:  Embossed adhesive tape, with 3/16 inch (5 mm) white letters on black background. 


.2
seq level2 \h \r0 
WIRE MARKERS



A.
Description:
 Tape type wire markers.



B.seq level3 \h \r0 
Locations:  Each conductor at panelboard gutters, pull boxes and each load connection.



C.
Legend:




1.
Power and Lighting Circuits:
Branch circuit or feeder number indicated on drawings.


.3 
UNDERGROUND WARNING TAPE seq level2 \h \r0 

seq level3 \h \r0 


A.
Description:
4 inch  wide plastic tape, detectable type, colored red with suitable warning legend describing buried electrical lines.


seq level3 \h \r0 
3

seq level1 \h \r0 

seq level2 \h \r0  PART 3 
EXECUTION


.1

PREPARATION



A.
Degrease and clean surfaces to receive nameplates.

.2

seq level2 \h \r0 

APPLICATION



A.
Install nameplate and label parallel to equipment lines.



B.
Secure nameplate to equipment front using screws.


C.
Secure nameplate to inside surface of door on panelboard that is recessed in finished locations.



D.
Identify underground conduits using underground warning tape.  Install one tape per trench at 3 inches below finished grade.


seq level3 \h \r0 



END OF SECTION

1
1

